## Summary
COST Summary
Scenario | Measure | Year 1 | Year 2 | Year 3 | Total | Scenario | Measure | Year 1 | Year 2 | Year 3 | Total
1 (G, E) | 52021924.6298 |  |  |  |  | 3 (G, E+R) | 44458596.258
| Equipment Costs | 5975000 | 3804163 | 6845102.26 | 16624265.26 |  | Equipment Costs | 4868950 | 3381122 | 5225554.74 | 13475626.74
| Servers | 1880000 | 1148163 | 2149102.26 | 5177265.26 |  | Servers | 1543950 | 1021122 | 1640554.74 | 4205626.74
| Routers (Shelves | 3420000 | 2251000 | 3951000 | 9622000 |  | Routers (Shelves | 2775000 | 2000000 | 3025000 | 7800000
| Racks | 675000 | 405000 | 745000 | 1825000 |  | Racks | 550000 | 360000 | 560000 | 1470000
| Operations Cost | 23567244.5828 | 5165657.7877 | 6664756.9993 | 35397659.3698 |  | Operations Cost | 19868492.9973 | 4875775.7327 | 6238700.788 | 30982969.518
| Power | 232534.3196 | 376659.4056 | 636881.5688 | 1246075.294 |  | Power | 190737.3816 | 319194.8224 | 518851.0292 | 1028783.2332
| Labor | 2028000 | 2088840 | 2151505.2 | 6268345.2 |  | Labor | 2028000 | 2088840 | 2151505.2 | 6268345.2
| Other Expenses | 859628.5426 | 2700158.3821 | 3876370.2305 | 7436157.1552 |  | Expenses | 823421.0708 | 2467740.9103 | 3568344.5588 | 6859506.5399
| Facility | 20447081.7207 | 0 | 0 | 20447081.7207 |  | Facility | 16826334.5449 | 0 | 0 | 16826334.5449
2 (G+D, E) | 45205646.8344 |  |  |  |  | 4 (G+D, E+R) | 41232977.8421
| Equipment Costs | 5279000 | 3675335 | 6631102.26 | 15585437.26 |  | Equipment Costs | 3928950 | 3732122 | 5427554.74 | 13088626.74
| Servers | 1880000 | 1142335 | 2149102.26 | 5171437.26 |  | Servers | 1543950 | 1021122 | 1640554.74 | 4205626.74
| Routers (Shelves | 2714000 | 2168000 | 3747000 | 8629000 |  | Routers (Shelves | 1860000 | 2346000 | 3222000 | 7428000
| Racks | 685000 | 365000 | 735000 | 1785000 |  | Racks | 525000 | 365000 | 565000 | 1455000
| Operations Cost | 18441355.9428 | 4873254.423 | 6305599.2086 | 29620209.5744 |  | Operations Cost | 17493656.0489 | 4609620.8466 | 6041074.2066 | 28144351.1021
| Power | 127568.9404 | 275168.1524 | 486401.4896 | 889138.5824 |  | Power | 111399.1172 | 258767.646 | 457752.1576 | 827918.9208
| Labor | 2028000 | 2088840 | 2151505.2 | 6268345.2 |  | Labor | 2028000 | 2088840 | 2151505.2 | 6268345.2
| Expenses | 809916.4311 | 2509246.2706 | 3667692.519 | 6986855.2207 |  | Expenses | 800693.3611 | 2262013.2006 | 3431816.849 | 6494523.4107
| Facility | 15475870.5713 | 0 | 0 | 15475870.5713 |  | Facility | 14553563.5706 | 0 | 0 | 14553563.5706
Scenario Comparison - (3-Year)Total Cost
|  | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4
| Servers | 5177265.26 | 5171437.26 | 4205626.74 | 4205626.74
| Routers | 9622000 | 8629000 | 7800000 | 7428000
| Racks | 1825000 | 1785000 | 1470000 | 1455000
| Power | 1246075.294 | 889138.5824 | 1028783.2332 | 827918.9208
| Labor | 6268345.2 | 6268345.2 | 6268345.2 | 6268345.2
| Other Expenses | 7436157.1552 | 6986855.2207 | 6859506.5399 | 6494523.4107
| Facility | 20447081.7207 | 15475870.5713 | 16826334.5449 | 14553563.5706 | 3-year
Scenario Comparison - Total (3-Year) Total Equipment Needs
|  | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4
| Servers | 2158 | 1180 | 1754 | 1357
| Router Cards | 1514 | 1127 | 1256 | 1098
| Router Shelves | 54 | 46 | 40 | 37
| Racks | 365 | 261 | 294 | 252
Power Use Comparison
|  | Year 1 | Year 2 | Year 3
| scenario 1 | 2262007 | 3664002 | 6195346
| scenario 2 | 1240943 | 2676733 | 4731532
| scenario 3 | 1855422 | 3105008 | 5047189
| scenario 4 | 1083649 | 2517195 | 4452842

## User Profile
User Profile Calculations
Period | Total Users | User Growth | User Growth Rate (%) | % Total Active Users | Average Active Users | Active User Growth | Active User Growth Rate (%)
2021-01-01 | 5000000 | - | - | 30% | 1500000 |  | -
2021-07-01 | 6670000 | 1670000 | 33.4% | 30% | 2001000 | 501000 | 33.4%
2022-01-01 | 8890000 | 2220000 | 33.28% | 45% | 4000500 | 1999500 | 99.93%
2022-07-01 | 11850000 | 2960000 | 33.3% | 45% | 5332500 | 1332000 | 33.3%
2023-01-01 | 15800000 | 3950000 | 33.33% | 60% | 9480000 | 4147500 | 77.78%
2023-07-01 | 21070000 | 5270000 | 33.35% | 60% | 12642000 | 3162000 | 33.35%
2024-01-01 | 28090000 | 7020000 | 33.32% | 60% | 16854000 | 4212000 | 33.32%

## CPU (Workload)
CPU (Active Workload) Calculations
Equivalent Peak Hours | 7.545
NOTE: Based on playback curve in graph |  | Average percent of activity/day |  |  | 4.1667
|  | Average peak percent of activity/day |  |  | 7.275
|  | Peak-to-Average Ratio |  |  | 1.746
|  | Peak Hrs/day |  |  | 4
Request Rates (per User/per Hour) |  | Streaming | Download | Permission | Total
|  | 24 | 4 | 16 | 44
Required TPS | Period | Active Users | Streaming | Download | Permission | Total
| 2021-01-01 | 1500000 | 3143.75 | 523.9583 | 2095.8333 | 5763.5417
| 2021-07-01 | 2001000 | 4193.7625 | 698.9604 | 2795.8417 | 7688.5646
| 2022-01-01 | 4000500 | 8384.3812 | 1397.3969 | 5589.5875 | 15371.3656
| 2022-07-01 | 5332500 | 11176.0312 | 1862.6719 | 7450.6875 | 20489.3906
| 2023-01-01 | 9480000 | 19868.5 | 3311.4167 | 13245.6667 | 36425.5833
| 2023-07-01 | 12642000 | 26495.525 | 4415.9208 | 17663.6833 | 48575.1292
| 2024-01-01 | 16854000 | 35323.175 | 5887.1958 | 23548.7833 | 64759.1542
[7 empty] | Period | Streaming | Downloads | Permission Requests
[7 empty] | Year 1 | 8384.3812 | 1397.3969 | 5589.5875
[7 empty] | Year 2 | 19868.5 | 3311.4167 | 13245.6667
[7 empty] | Year 3 | 35323.175 | 5887.1958 | 23548.7833
Note on C5: Crash Davis: Determined by taking the the estimated peak %'s per day and averaging those

## Bandwidth
Bandwidth Calculations
Streaming Music | (1 TPS is equivalent to streaming 1 full song/sec) | [5 empty] | TPS by Bit Rate |  |  | Gbps |  |  | Total Needed Bandwidth (Gbps)
| Song Duration (s) |  | 192 |  |  | Total Streaming TPS | Low Rate | Standard | High | Low Rate | Standard | High |  | Period | Streaming | Downloads | Permission Requests
| Song Rates | Kbps | Song Size (Kb) | % of stream | 2021-01-01 | 3143.75 | 628.75 | 1886.25 | 628.75 | 13.5206 | 69.5347 | 28.9728 | 112.0282 | Year 1 | 298.7791 | 80.4901 | 8.9433
| Low | 112 | 21504 | 20% | 2021-07-01 | 4193.7625 | 838.7525 | 2516.2575 | 838.7525 | 18.0365 | 92.7593 | 38.6497 | 149.4456 | Year 2 | 708.018 | 190.7376 | 21.1931
| Standard | 192 | 36864 | 60% | 2022-01-01 | 8384.3812 | 1676.8762 | 5030.6287 | 1676.8762 | 36.0595 | 185.4491 | 77.2705 | 298.7791 | Year 3 | 1258.7484 | 339.1025 | 37.6781
| High | 240 | 46080 | 20% | 2022-07-01 | 11176.0312 | 2235.2062 | 6705.6187 | 2235.2062 | 48.0659 | 247.1959 | 102.9983 | 398.2601
[5 empty] | 2023-01-01 | 19868.5 | 3973.7 | 11921.1 | 3973.7 | 85.4504 | 439.4594 | 183.1081 | 708.018
[5 empty] | 2023-07-01 | 26495.525 | 5299.105 | 15897.315 | 5299.105 | 113.952 | 586.0386 | 244.1828 | 944.1733
[5 empty] | 2024-01-01 | 35323.175 | 7064.635 | 21193.905 | 7064.635 | 151.9179 | 781.2921 | 325.5384 | 1258.7484
Downloading Music | (1 TPS is equivalent to downloading 1 full song/sec)
| Song Size (GB) |  | 0.0072 | [8 empty] | Download TPS | Total Needed Bandwidth (Gbps)
| Downloads/Hr/Active User |  | 4 | [7 empty] | 2021-01-01 | 523.9583 | 30.18
[11 empty] | 2021-07-01 | 698.9604 | 40.2601
[11 empty] | 2022-01-01 | 1397.3969 | 80.4901
[11 empty] | 2022-07-01 | 1862.6719 | 107.2899
[11 empty] | 2023-01-01 | 3311.4167 | 190.7376
[11 empty] | 2023-07-01 | 4415.9208 | 254.357
[11 empty] | 2024-01-01 | 5887.1958 | 339.1025
Playback Authorization (Request-Respond)
| Request Size (GB) |  | 0.0002 | [8 empty] | Permission Request TPS | Total Needed Bandwidth (Gbps)
| Requests/Hr/Active User |  | 16 | [7 empty] | 2021-01-01 | 2095.8333 | 3.3533
[11 empty] | 2021-07-01 | 2795.8417 | 4.4733
[11 empty] | 2022-01-01 | 5589.5875 | 8.9433
[11 empty] | 2022-07-01 | 7450.6875 | 11.9211
[11 empty] | 2023-01-01 | 13245.6667 | 21.1931
[11 empty] | 2023-07-01 | 17663.6833 | 28.2619
[11 empty] | 2024-01-01 | 23548.7833 | 37.6781
Total Aggregate Bandwidth
Total Needed Bandwidth (Gbps)
[12 empty] | 2021-01-01 | 145.5615
[12 empty] | 2021-07-01 | 194.179
[12 empty] | 2022-01-01 | 388.2125
[12 empty] | 2022-07-01 | 517.4711
[12 empty] | 2023-01-01 | 919.9486
[12 empty] | 2023-07-01 | 1226.7923
[12 empty] | 2024-01-01 | 1635.5289

## Memory
Memory Calculations
Streaming Music | Assume that DRM-on-the-fly is performed in memory
| (1 TPS is equivalent to streaming 1 full song/sec) |  |  |  |  | TPS (Songs) per Bit Rate Type |  |  |  | GB RAM |  |  | Total Needed Memory (GB)
| Song Duration (s) |  | 192 |  |  | Total Streaming TPS (Songs) | Low Rate Songs / sec | Standard Rate Songs / sec | High Rate Songs / sec | Low Rate | Standard | High |  | Period | Streaming | Downloads | Permission Requests
| Song Rates | Kbps | Song Size (Kb) | % of stream | 2021-01-01 | 3143.75 | 628.75 | 1886.25 | 628.75 | 1.6901 | 5.0702 | 1.6901 | 8.4504 | Year 1 | 22.5372 | 10.0613 | 1.1179
| Low | 112 | 21504 | 20% | 2021-07-01 | 4193.7625 | 838.7525 | 2516.2575 | 838.7525 | 2.2546 | 6.7637 | 2.2546 | 11.2728 | Year 2 | 53.4065 | 23.8422 | 2.6491
| Standard | 192 | 36864 | 60% | 2022-01-01 | 8384.3812 | 1676.8762 | 5030.6287 | 1676.8762 | 4.5074 | 13.5223 | 4.5074 | 22.5372 | Year 3 | 94.9487 | 42.3878 | 4.7098
| High | 240 | 46080 | 20% | 2022-07-01 | 11176.0312 | 2235.2062 | 6705.6187 | 2235.2062 | 6.0082 | 18.0247 | 6.0082 | 30.0412
[5 empty] | 2023-01-01 | 19868.5 | 3973.7 | 11921.1 | 3973.7 | 10.6813 | 32.0439 | 10.6813 | 53.4065
[5 empty] | 2023-07-01 | 26495.525 | 5299.105 | 15897.315 | 5299.105 | 14.244 | 42.732 | 14.244 | 71.22
[5 empty] | 2024-01-01 | 35323.175 | 7064.635 | 21193.905 | 7064.635 | 18.9897 | 56.9692 | 18.9897 | 94.9487
Downloading Music | (1 TPS is equivalent to downloading 1 full song/sec)
| Song Size (GB) |  | 0.0072 | [8 empty] | Download TPS (# Songs) | Total Needed Memory (GB)
| Downloads/Hr/Active User |  | 4 | [7 empty] | 2021-01-01 | 523.9583 | 3.7725
[11 empty] | 2021-07-01 | 698.9604 | 5.0325
[11 empty] | 2022-01-01 | 1397.3969 | 10.0613
[11 empty] | 2022-07-01 | 1862.6719 | 13.4112
[11 empty] | 2023-01-01 | 3311.4167 | 23.8422
[11 empty] | 2023-07-01 | 4415.9208 | 31.7946
[11 empty] | 2024-01-01 | 5887.1958 | 42.3878
Playback Authorization (Request-Respond)
| Request Size (GB) |  | 0.0002 | [8 empty] | Permission Request TPS | Total Needed Memory (GB)
| Requests/Hr/Active User |  | 16 | [7 empty] | 2021-01-01 | 2095.8333 | 0.41917
[11 empty] | 2021-07-01 | 2795.8417 | 0.55917
[11 empty] | 2022-01-01 | 5589.5875 | 1.1179
[11 empty] | 2022-07-01 | 7450.6875 | 1.4901
[11 empty] | 2023-01-01 | 13245.6667 | 2.6491
[11 empty] | 2023-07-01 | 17663.6833 | 3.5327
[11 empty] | 2024-01-01 | 23548.7833 | 4.7098
Total Aggregate Bandwidth
Total Needed Memory (GB)
[12 empty] | 2021-01-01 | 12.6421
[12 empty] | 2021-07-01 | 16.8645
[12 empty] | 2022-01-01 | 33.7164
[12 empty] | 2022-07-01 | 44.9425
[12 empty] | 2023-01-01 | 79.8979
[12 empty] | 2023-07-01 | 106.5473
[12 empty] | 2024-01-01 | 142.0463

## Storage
Storage Calculations
Total Number of Songs in Library |  |  | 40000000 | Similar to Spotify and iTunes; remains consistent (new songs replace old songs)
Assumption: All songs in library available for streaming and download
Streaming Storage
| Bit Rate (Kbps) | Duration (s) | Song Size (GB) | Library Storage Needs (GB)
Low Bit-Rate | 112 | 192 | 0.002688 | 107520
Standard Bit-Rate | 192 | 192 | 0.004608 | 184320
High Bit-Rate | 240 | 192 | 0.00576 | 230400
Download Storage
|  |  | Song Size (GB) | Library Storage Needs (GB)
|  |  | 0.0072 | 288000
Permission Storage
No significant storage; requests and responses are assumed fire and forget; nothing stored (all in-memory processing)

## Scenario 1
Scenario 1: General Servers - Encryption Only (no Rate Adaptation)
General Notes on Architecture
All servers are general purpose servers; no mixing
Server Type (Large, X-Large) selected per service; all servers for a given service are homogenous
With no rate adaptation, all songs at all bit rates must be stored
Scale on an annual basis not on intermediate 6 month numbers
Total Infrastructure Capacity Summary
Infrastructure | Total Capacity (Cum) | Year 1 | Year 2 | Year 3
| Servers | 800 | 1279 | 2158
| Router Cards | 532 | 891 | 1514
| Router Shelves | 20 | 32 | 54
| Racks | 135 | 216 | 365
Total Cost Summary
Equipment Costs (Annual) |  | Year 1 | Year 2 | Year 3
| Servers | 1880000 | 1148163 | 2149102.26
| Routers | 3420000 | 2251000 | 3951000
| Racks | 675000 | 405000 | 745000
| Total Equipment Costs | 5975000 | 3804163 | 6845102.26
Operating Costs
| Power | 232534.3196 | 376659.4056 | 636881.5688
| Labor | 2028000 | 2088840 | 2151505.2
| Other Expenses | 859628.5426 | 2700158.3821 | 3876370.2305
| Capital Costs (Land and Facility Construction) | 20447081.7207 | 0 | 0
| Total Operating Costs | 23567244.5828 | 5165657.7877 | 6664756.9993
Total Lifecycle Cost | 52021924.6298 | 29542244.5828 | 8969820.7877 | 13509859.2593
Servers
Streaming Storage Servers
[6 empty] | Resource Calculations | [31 empty] | Cost Calculations
Memory in this scenario (used for encryption)was not evaluated since needed memory volumes are easily satisfied with the number of storage and/or bandwidth-based server quantities | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
Streaming | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 1111007 | 606631 | 1484106.58 | 3201744.58
| Storage (GB) | 522240 | 522240 | 522240 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 349 | 124 | 367 | 840
| TPS | 8384.3812 | 19868.5 | 35323.175 |  | Large | 23 | 15 | 12 | 820 | 399 | 820 | 75 | 1867632 |  | Large | 27 | 18 | 14 | 820 | 945 | 945 | 125 | 12 | 2152332 |  | Large | 48 | 32 | 24 | 820 | 1679 | 1679 | 734 | 67 | 3824090 |  | Large | 697000 | 375000 | 95996 | 0 | 1167996 |  | Large | 108375 | 60000 | 110630 | 139400 | 418405 | Large | 649105.56 | 335000 | 196558 | 161075 | 1341738.56 | 1679 | 154 | 7844054 | 2928139.56 |  | New Racks | 50 | 18 | 53 | 121
| Bandwidth (Gbps) | 298.7791 | 708.018 | 1258.7484 |  | Xlarge | 10 | 7 | 5 | 349 | 200 | 349 | 50 | 794882 |  | Xlarge | 2 | 8 | 6 | 349 | 473 | 473 | 124 | 18 | 1077305 |  | Xlarge | 20 | 14 | 10 | 349 | 840 | 840 | 367 | 53 | 1913184 |  | Xlarge | 820150 | 250000 | 40857 | 0 | 1111007 |  | Xlarge | 297228 | 90000 | 55373 | 164030 | 606631 | Xlarge | 897292.98 | 265000 | 98338 | 223475.6 | 1484106.58 | 840 | 121 | 3785371 | 3201744.58 | Use XL servers | Power | 794882 | 1077305 | 1913184 | 3785371
Download Storage Servers
Memory in this scenario (used for encryption)was not evaluated since needed memory volumes are easily satisfied with the number of storage and/or bandwidth-based server quantities | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
Download | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 613677 | 112717 | 227387.9 | 953781.9
| Storage (GB) | 288000 | 288000 | 288000 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 192 | 0 | 35 | 227
| TPS | 1397.3969 | 3311.4167 | 5887.1958 |  | Large | 4 | 3 | 2 | 452 | 108 | 452 | 42 | 1029475 |  | Large | 5 | 3 | 3 | 452 | 255 | 452 | 0 | 0 | 1029475 |  | Large | 8 | 6 | 4 | 452 | 453 | 453 | 1 | 1 | 1031753 |  | Large | 384200 | 210000 | 52915 | 0 | 647115 |  | Large | 0 | 0 | 52915 | 76840 | 129755 | Large | 884.34 | 5000 | 53032 | 76840 | 135756.34 | 453 | 43 | 3090703 | 912626.34 |  | New Racks | 28 | 0 | 5 | 33
| Bandwidth (Gbps) | 80.4901 | 190.7376 | 339.1025 |  | Xlarge | 2 | 2 | 1 | 192 | 54 | 192 | 28 | 437299 |  | Xlarge | 0 | 2 | 1 | 192 | 128 | 192 | 0 | 0 | 437299 |  | Xlarge | 4 | 3 | 2 | 192 | 227 | 227 | 35 | 5 | 517015 |  | Xlarge | 451200 | 140000 | 22477 | 0 | 613677 |  | Xlarge | 0 | 0 | 22477 | 90240 | 112717 | Xlarge | 85572.9 | 25000 | 26575 | 90240 | 227387.9 | 227 | 33 | 1391613 | 953781.9 | Use XL servers | Power | 437299 | 437299 | 517015 | 1391613
Web/App Servers
[38 empty] | Cost Calculations | [6 empty] | Cost Calculations
These handle all the incoming requests (transactions) and route the outbound responses; they handle all the permission requests directly (ie., no routing to storage server clusters); transactions performed in memory | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
[6 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 823971 | 1299545 | 1930875.38 | 4054391.38
| Storage (GB) | 0 | 0 | 0 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 259 | 355 | 477 | 1091
| TPS | 15371.3656 | 36425.5833 | 64759.1542 |  | Large | 21 | 14 | 11 | 0 | 518 | 518 | 48 | 1179797 |  | Large | 49 | 33 | 25 | 0 | 1227 | 1227 | 709 | 65 | 2794615 |  | Large | 87 | 58 | 44 | 0 | 2181 | 2181 | 954 | 87 | 4967446 |  | Large | 440300 | 240000 | 60642 | 0 | 740942 |  | Large | 614703 | 325000 | 143643 | 88060 | 1171406 | Large | 843660.36 | 435000 | 255327 | 211000.6 | 1744987.96 | 2181 | 200 | 8941858 | 3657335.96 |  | New Racks | 37 | 51 | 69 | 157
| Bandwidth (Gbps) | 388.2125 | 919.9486 | 1635.5289 |  | Xlarge | 9 | 6 | 5 | 0 | 259 | 259 | 37 | 589898 |  | Xlarge | 12 | 14 | 11 | 0 | 614 | 614 | 355 | 51 | 1398446 |  | Xlarge | 36 | 24 | 18 | 0 | 1091 | 1091 | 477 | 69 | 2484862 |  | Xlarge | 608650 | 185000 | 30321 | 0 | 823971 |  | Xlarge | 850935 | 255000 | 71880 | 121730 | 1299545 | Xlarge | 1166236.38 | 345000 | 127722 | 291917 | 1930875.38 | 1091 | 157 | 4473206 | 4054391.38 | Use XL Servers | Power | 589898 | 1398446 | 2484862 | 4473206
Totals
Sum of all Servers | [37 empty] | Cost Calculations | [6 empty] | Cost Calculations
[6 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 1 | [5 empty] | Year 3 | [10 empty] | Total Cost Summary
User Interaction | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 2548655 | 2018893 | 3642369.86 | 8209917.86
| Storage (GB) | 810240 | 810240 | 810240 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 800 | 479 | 879 | 2158
| TPS | 25153.1437 | 59605.5 | 105969.525 |  | Large | [5 empty] | 1790 | 165 | 4076904 |  | Large | [5 empty] | 2624 | 834 | 77 | 5976422 |  | Large | [5 empty] | 4313 | 1689 | 155 | 9823289 |  | Large | 1521500 | 825000 | 209553 | 0 | 2556053 |  | Large | 723078 | 385000 | 307188 | 304300 | 1719566 | Large | 1493650.26 | 775000 | 504917 | 448915.6 | 3222482.86 | [5 empty] | New Racks | 115 | 69 | 127 | 311
| Bandwidth (Gbps) | 767.4817 | 1818.7042 | 3233.3798 |  | Xlarge | [5 empty] | 800 | 115 | 1822079 |  | Xlarge | [5 empty] | 1279 | 479 | 69 | 2913050 |  | Xlarge | [5 empty] | 2158 | 879 | 127 | 4915061 |  | Xlarge | 1880000 | 575000 | 93655 | 0 | 2548655 |  | Xlarge | 1148163 | 345000 | 149730 | 376000 | 2018893 | Xlarge | 2149102.26 | 635000 | 252635 | 605632.6 | 3642369.86 | [5 empty] | Power | 1822079 | 2913050 | 4915061 | 9650190
Routers
Single Tier Network
Use Gig-E to connect all servers to routers
Use fiber (OC-48 or OC-192) to connect router-to-router and router-to-internet
Assume perfect load-balancing between connectivity
Assume following Shelf Configuration: 20 GigE, 8 OC48 and 4 OC192 cards
Assume at any time only 50% of ports are active (fully 1:1 redundancy)
Router-to-Internet | The total of all inbound and outbound from/to internet
Resource Needs |  | Year 1 | Year 2 | Year 3 |  | Card Type | # Ports Required
| Bandwidth (Gbps) | 388.2125 | 919.9486 | 1635.5289 |  |  | Year 1 | Year 2 | Year 3
[6 empty] | Gig-E | 1036 | 2454 | 4362
[6 empty] | OC-48 | 416 | 982 | 1746
[6 empty] | OC-192 | 104 | 246 | 438
Router-to-Server
Since the servers only have Gig-E NICs, all connections with servers are via Gig-E router cards
# Ports needed determined by the MAX of ports needed based on BW (*2) vs physical NICs on each server
Other transactional messaging (e.g. IPC messages, etc. between servers) is considered negligible and not estimated
Resource Needs |  | Year 1 | Year 2 | Year 3 |  |  | # Ports Required
| Servers | 800 | 1279 | 2158 |  |  | Year 1 | Year 2 | Year 3
[6 empty] | Gig-E | 3200 | 5116 | 8632 | These are inbound from servers
Total Router Traffic
Per Cost Analysis, OC48's are most cost-effective for non-server interconnects, so these are factored | [6 empty] | Total # Ports Required |  |  |  |  | Total # Cards |  |  | Total # Shelves |  |  | Total # racks |  |  | Power Consumption kWh (total per year) |  |  |  | Year 1 | [6 empty] | Year 2 | [6 empty] | Year 3 | [6 empty] | Total Cost Summary
Router-to-Router (for redundancy and further failover) | [6 empty] | Year 1 | Year 2 | Year 3 |  |  | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  |  | Year 1 | Year 2 | Year 3 | 3-year Total
Assume 1:1 redundancy between shelves (set up as a ring), so a total of four card slots reserved for inter-shelf redundancy; means 4 cards per shelf total. Use OC-192s to maximize the number of in-shelf card failures it can handle. | [5 empty] | Gig-E | 3200 | 5116 | 8632 |  | Gig-E | 400 | 640 | 1079 | 20 | 32 | 54 |  |  |  | 189216 | 302746 | 510411 |  | 3220000 | 200000 | 100000 | 22613 | 0 | 3542613 |  | 2131000 | 120000 | 60000 | 38599 | 684000 | 3033599 |  | 3731000 | 220000 | 110000 | 65807 | 1134200 | 5261007 |  | Cost | 3542613 | 3033599 | 5261007 | 11837219
[6 empty] | OC-48 | 416 | 982 | 1746 |  | OC-48 | 52 | 123 | 219 | 7 | 16 | 28 |  |  |  | 61496 | 145460 | 258990 | [22 empty] | New Cards | 532 | 359 | 623 | 1514
[6 empty] | OC-192 | NA | NA | NA |  | OC-192 | 80 | 128 | 216 | NA | NA | NA |  |  |  | 189216 | 302746 | 510884 | [22 empty] | New Shelves | 20 | 12 | 22 | 54
[6 empty] | Totals | 3616 | 6098 | 10378 |  | Totals | 532 | 891 | 1514 | 20 | 32 | 54 | 20 | 32 | 54 | 439928 | 750952 | 1280285 | [22 empty] | New Racks | 20 | 12 | 22 | 54
[46 empty] | Power | 439928 | 750952 | 1280285 | 2471165
Data Center Costs
This includes costs not directly tied to server/switch equipment.
Assume a Tier III Data Center for availability/reliability
Most of this approach came from Uptime Institute True TCO Calculator
|  | Year 1 | Year 2 | Year 3
Capital Costs
Facility Construction Costs
| Square Footage | 8640 | 13824 | 23360
| Land Costs (assume 5 acres @ $100K/acre) | 500000 | 0 | 0
| kW-Related Infrastructure Costs | 16832811.6605 | 0 | 0
| Other Facility Costs | 1131840 | 0 | 0
| Interest | 369293.0332 | 0 | 0
| Architecture/Engineering Fees | 898232.583
Internet Fiber Last Mile Cost
| Number of Single-Mode Fiber Strands | 1746
| Number of Cables (144 strands/cable) | 13
| Total Cable Length (# cables * fiber run * 110%) | 75504
| Cable Cost | 148742.88
| Installation Costs | 250000
| TOTAL Internet Last Mile | 398742.88 | 0 | 0
| Internal Cabling Cost | 280800 | 0 | 0
| Fire Suppression | 35361.5639 | 0 | 0
| Total Capital Costs | 20447081.7207 | 0 | 0
Annual Operating Expenses
Energy and Power Use/Costs
| Total Electricity Use (kW) | 516.44 | 836.5301 | 1414.4626
| IT Load (kWh/yr) | 2262007 | 3664002 | 6195346
| Cooling and Auxiliaries (kWh/yr) | 2262007 | 3664002 | 6195346
| Total Consumption (kWh/yr) | 4524014 | 7328004 | 12390692
| Annual Energy Cost | 232534.3196 | 376659.4056 | 636881.5688
| Annual Internet Transit Cost | 655157.7253 | 1435687.5649 | 1932066.8133
| Annual HW Vendor Support Costs | 0 | 1060000 | 1739832.6
| Property Taxes | 204470.8172 | 204470.8172 | 204470.8172
| Total Annual Operating Expenses | 1092162.8622 | 3076817.7877 | 4513251.7993
Labor Costs
| IT site management staff | 390000 | 401700 | 413751
| Facilities site management staff | 520000 | 535600 | 551668
| Maintenance | 416000 | 428480 | 588298.7552
| Security | 702000 | 723060 | 744751.8
| Janitorial and landscaping | 34560 | 35596.8 | 36664.704
| Total Labor Costs | 2028000 | 2088840 | 2151505.2
Total Data Center Costs |  | 23567244.5828 | 5165657.7877 | 6664756.9993
Labor Estimates
|  |  | IT site | Facilities site
|  |  | Mgmt | Mgmt | Maintenance | Security
| Salary per person | k$/year | 100 | 100 | 80 | 60
| People per shift | # | 3 | 4 | 4 | 3
| Shifts per day | # | 1 | 1 | 1 | 3
| benefits percentage | % | 30% | 30% | 30% | 30%
| Total cost per year | k$/year | 390 | 520 | 416 | 702
| Janitorial and Landscaping Costs |  |  | 4 | per square foot
Note on W41: Crash Davis: Set to the Storage Servers per assumption
Note on AQ41: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W50: Crash Davis: Set to the Storage Servers per assumption
Note on AQ50: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W60: Crash Davis: Set to the Storage Servers per assumption
Note on AQ60: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W71: Crash Davis: Set to the Storage Servers per assumption
Note on AQ71: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on H89: Crash Davis: This is total bw needed /usable bw per card port *2 (for redundancy)
Note on H101: Crash Davis: This is # servers * # NICs per server # servers has built-in-redundancy for BW
Note on H107: Crash Davis: This is total bw needed /usable bw per card port *2 (for redundancy)
Note on B125: Crash Davis: This assumes a total square footage based on a per-rack sf estimate For a Tier III, the standard is 1:1 add'l space compared to electrically active space
Note on B127: Crash Davis: Uptime Institute figure of 23801 per kW of IT Load
Note on B129: Crash Davis: Interest on the Construction and Land Costs @ 2% real discount rate (assumed)
Note on B130: Crash Davis: Assumed at 5% of infrastructure and facility costs
Note on B131: Crash Davis: This is a first year cost, since it is expensive to lay additional fiber later
Note on C132: Crash Davis: Based on max number of internet-to-router OC-48 ports (1 strand per port)
Note on B136: Crash Davis: This is just an approximation; too many variables to establish a basis estimate
Note on B138: Crash Davis: Estimated at the equivalent of $65/sf of electrically active space
Note on B139: Crash Davis: Estimated at $50/sf of electrically active area
Note on B145: Crash Davis: Equal to the IT Load (conservation of energy)
Note on B148: Crash Davis: This is calculated by taking the BW at year-end-BW at start and dividing by 2 as an approximate average bandwidth over the year, then multiplying by the IP transit cost (Mbps/month)
Note on B149: Crash Davis: A % of the cost of prior year total capacity (servers and routers)
Note on B150: Crash Davis: Estimated at 1% of Capital Costs/year
Note on A152: Crash Davis: 3% per annum COLA; Maintenance grows to 4 in year 3 due to increased capacity

## Scenario 2
Scenario 2: Dedicated Storage Servers - Encryption Only (no Rate Adaptation)
General Notes on Architecture
Server Type (Large, X-Large) selected per service; all servers for a given service are homogenous
NAS Servers are replaced for streaming and download servers
With no rate adaptation, all songs at all bit rates must be stored
Total Infrastructure Capacity Summary
Infrastructure | Total Capacity (Cum) | Year 1 | Year 2 | Year 3
| Servers and NAS | 281 | 665 | 1180
| Router Cards | 314 | 636 | 1127
| Router Shelves | 22 | 26 | 46
| Racks | 71 | 141 | 261
Total Cost Summary
Equipment Costs (Annual) |  | Year 1 | Year 2 | Year 3
| Servers | 1880000 | 1142335 | 2149102.26
| Routers | 2714000 | 2168000 | 3747000
| Racks | 685000 | 365000 | 735000
| Total Equipment Costs | 5279000 | 3675335 | 6631102.26
Operating Costs
| Power | 127568.9404 | 275168.1524 | 486401.4896
| Labor | 2028000 | 2088840 | 2151505.2
| Other Expenses | 809916.4311 | 2509246.2706 | 3667692.519
| Capital Costs (Land and Facility Construction) | 15475870.5713 | 0 | 0
| Total Operating Costs | 18441355.9428 | 4873254.423 | 6305599.2086
Total Lifecycle Cost | 45205646.8344 | 23720355.9428 | 8548589.423 | 12936701.4686
Servers
Streaming Storage Servers
[6 empty] | Resource Calculations | [31 empty] | Cost Calculations
Memory in this scenario (used for encryption)was not evaluated since needed memory volumes are easily satisfied with the number of storage and/or bandwidth-based server quantities | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
Streaming | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 3113573 | 4832172 | 10055301 | 18001046
| Storage (GB) | 522240 | 522240 | 522240 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 17 | 23 | 47 | 87
| TPS | 8384.3812 | 19868.5 | 35323.175 |  | Large | 12 | 8 | 6 | 820 | 399 | 820 | 75 | 1867632 |  | Large | 27 | 18 | 14 | 820 | 945 | 945 | 125 | 12 | 2152332 |  | Large | 48 | 32 | 24 | 820 | 1679 | 1679 | 734 | 67 | 3824090 |  | Large | 697000 | 375000 | 95996 | 0 | 1167996 |  | Large | 106250 | 60000 | 110630 | 139400 | 416280 | Large | 649105.56 | 335000 | 196558 | 160650 | 1341313.56 | 1679 | 154 | 7844054 | 2925589.56 |  | New Racks | 9 | 12 | 24 | 45
| Bandwidth (Gbps) | 298.7791 | 708.018 | 1258.7484 |  | Xlarge | 5 | 4 | 3 | 349 | 200 | 349 | 50 | 794882 |  | Xlarge | 7 | 8 | 6 | 349 | 473 | 473 | 124 | 18 | 1077305 |  | Xlarge | 20 | 14 | 10 | 349 | 840 | 840 | 367 | 53 | 1913184 |  | Xlarge | 820150 | 250000 | 40857 | 0 | 1111007 |  | Xlarge | 291400 | 90000 | 55373 | 164030 | 600803 | Xlarge | 897292.98 | 265000 | 98338 | 222310 | 1482940.98 | 840 | 121 | 3785371 | 3194750.98 |  | Power | 166790 | 392448 | 686784 | 1246022
[6 empty] | NAS |  |  |  | 6 | 17 | 17 | 9 | 166790 |  | NAS |  |  |  | 6 | 40 | 40 | 23 | 12 | 392448 |  | NAS |  |  |  | 6 | 70 | 70 | 47 | 24 | 686784 |  | NAS | 3060000 | 45000 | 8573 | 0 | 3113573 |  | NAS | 4140000 | 60000 | 20172 | 612000 | 4832172 | NAS | 8460000 | 120000 | 35301 | 1440000 | 10055301 | 70 | 45 | 1246022 | 18001046 | Use NAS
Download Storage Servers
Memory in this scenario (used for encryption)was not evaluated since needed memory volumes are easily satisfied with the number of storage and/or bandwidth-based server quantities | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
Download | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 917521 | 1280547 | 2780582 | 4978650
| Storage (GB) | 288000 | 288000 | 288000 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 5 | 6 | 13 | 24
| TPS | 1397.3969 | 3311.4167 | 5887.1958 |  | Large | 2 | 2 | 1 | 452 | 108 | 452 | 42 | 1029475 |  | Large | 5 | 3 | 3 | 452 | 255 | 452 | 0 | 0 | 1029475 |  | Large | 8 | 6 | 4 | 452 | 453 | 453 | 1 | 1 | 1031753 |  | Large | 384200 | 210000 | 52915 | 0 | 647115 |  | Large | 0 | 0 | 52915 | 76840 | 129755 | Large | 884.34 | 5000 | 53032 | 76840 | 135756.34 | 453 | 43 | 3090703 | 912626.34 |  | New Racks | 3 | 3 | 7 | 13
| Bandwidth (Gbps) | 80.4901 | 190.7376 | 339.1025 |  | Xlarge | 1 | 1 | 1 | 192 | 54 | 192 | 28 | 437299 |  | Xlarge | 1 | 2 | 1 | 192 | 128 | 192 | 0 | 0 | 437299 |  | Xlarge | 4 | 3 | 2 | 192 | 227 | 227 | 35 | 5 | 517015 |  | Xlarge | 451200 | 140000 | 22477 | 0 | 613677 |  | Xlarge | 0 | 0 | 22477 | 90240 | 112717 | Xlarge | 85572.9 | 25000 | 26575 | 90240 | 227387.9 | 227 | 33 | 1391613 | 953781.9 |  | Power | 49056 | 107923 | 186413 | 343392
[6 empty] | NAS |  |  |  | 4 | 5 | 5 | 3 | 49056 |  | NAS |  |  |  | 4 | 11 | 11 | 6 | 3 | 107923 |  | NAS |  |  |  | 4 | 19 | 19 | 13 | 7 | 186413 |  | NAS | 900000 | 15000 | 2521 | 0 | 917521 |  | NAS | 1080000 | 15000 | 5547 | 180000 | 1280547 | NAS | 2340000 | 35000 | 9582 | 396000 | 2780582 | 19 | 13 | 343392 | 4978650 | Use NAS
Web/App Servers
[38 empty] | Cost Calculations | [6 empty] | Cost Calculations
These handle all the incoming requests (transactions) and route the outbound responses; they handle all the permission requests directly (ie., no routing to storage server clusters); transactions performed in memory | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
[6 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 823971 | 1299545 | 1930875.38 | 4054391.38
| Storage (GB) | 0 | 0 | 0 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 259 | 355 | 477 | 1091
| TPS | 15371.3656 | 36425.5833 | 64759.1542 |  | Large | 21 | 14 | 11 | 0 | 518 | 518 | 48 | 1179797 |  | Large | 49 | 33 | 25 | 0 | 1227 | 1227 | 709 | 65 | 2794615 |  | Large | 87 | 58 | 44 | 0 | 2181 | 2181 | 954 | 87 | 4967446 |  | Large | 440300 | 240000 | 60642 | 0 | 740942 |  | Large | 614703 | 325000 | 143643 | 88060 | 1171406 | Large | 843660.36 | 435000 | 255327 | 211000.6 | 1744987.96 | 2181 | 200 | 8941858 | 3657335.96 |  | New Racks | 37 | 51 | 69 | 157
| Bandwidth (Gbps) | 388.2125 | 919.9486 | 1635.5289 |  | Xlarge | 9 | 6 | 5 | 0 | 259 | 259 | 37 | 589898 |  | Xlarge | 12 | 14 | 11 | 0 | 614 | 614 | 355 | 51 | 1398446 |  | Xlarge | 36 | 24 | 18 | 0 | 1091 | 1091 | 477 | 69 | 2484862 |  | Xlarge | 608650 | 185000 | 30321 | 0 | 823971 |  | Xlarge | 850935 | 255000 | 71880 | 121730 | 1299545 | Xlarge | 1166236.38 | 345000 | 127722 | 291917 | 1930875.38 | 1091 | 157 | 4473206 | 4054391.38 | Use XL Servers | Power | 589898 | 1398446 | 2484862 | 4473206
Totals
Sum of all Servers | [37 empty] | Cost Calculations | [6 empty] | Cost Calculations
[6 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 1 | [5 empty] | Year 3 | [10 empty] | Total Cost Summary
User Interaction | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 4855065 | 7412264 | 14766758.38 | 27034087.38
| Storage (GB) | 810240 | 810240 | 810240 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 281 | 384 | 537 | 1202
| TPS | 25153.1437 | 59605.5 | 105969.525 |  | Large | [5 empty] | 1790 | 165 | 4076904 |  | Large | [5 empty] | 2624 | 834 | 77 | 5976422 |  | Large | [5 empty] | 4313 | 1689 | 155 | 9823289 |  | Large | 1521500 | 825000 | 209553 | 0 | 2556053 |  | Large | 720953 | 385000 | 307188 | 304300 | 1717441 | Large | 1493650.26 | 775000 | 504917 | 448490.6 | 3222057.86 | [5 empty] | New Racks | 49 | 66 | 100 | 215
| Bandwidth (Gbps) | 767.4817 | 1818.7042 | 3233.3798 |  | Xlarge | [5 empty] | 800 | 115 | 1822079 |  | Xlarge | [5 empty] | 1279 | 479 | 69 | 2913050 |  | Xlarge | [5 empty] | 2158 | 879 | 127 | 4915061 |  | Xlarge | 1880000 | 575000 | 93655 | 0 | 2548655 |  | Xlarge | 1142335 | 345000 | 149730 | 376000 | 2013065 | Xlarge | 2149102.26 | 635000 | 252635 | 604467 | 3641204.26 | [5 empty] | Power | 805744 | 1898817 | 3358059 | 6062620
[6 empty] | NAS | [5 empty] | 22 | 12 | 215846 |  | NAS | [5 empty] | 51 | 29 | 15 | 500371 |  | Xlarge | [5 empty] | 89 | 60 | 31 | 873197 |  | NAS | 3960000 | 60000 | 11094 | 0 | 4031094 |  | Xlarge | 5220000 | 75000 | 25719 | 792000 | 6112719 | NAS | 10800000 | 155000 | 44883 | 1836000 | 12835883
Routers
Single Tier Network
Use Gig-E to connect all servers to routers
Use fiber (OC-48 or OC-192) to connect router-to-router and router-to-internet
Assume perfect load-balancing between connectivity
Assume following Shelf Configuration: 14 GigE, 12 OC48 and 6 OC192 cards
Assume at any time only 50% of ports are active (fully 1:1 redundancy)
Router-to-Internet
Resource Needs |  | Year 1 | Year 2 | Year 3 |  | Card Type | # Ports Required
| Bandwidth (Gbps) | 388.2125 | 919.9486 | 1635.5289 |  |  | Year 1 | Year 2 | Year 3
[6 empty] | Gig-E | 1036 | 2454 | 4362
[6 empty] | OC-48 | 416 | 982 | 1746
[6 empty] | OC-192 | 104 | 246 | 438
Router-to-Server
Since the servers only have Gig-E NICs, all connections with servers are via Gig-E router cards
# Ports needed determined by the MAX of ports needed based on BW (*2) vs physical NICs on each server
Other transactional messaging (e.g. IPC messages, etc. between servers) is considered negligible and not estimated
Resource Needs |  | Year 1 | Year 2 | Year 3 |  |  | # Ports Required
| XLarge Servers | 259 | 614 | 1091 |  |  | Year 1 | Year 2 | Year 3
| NAS Servers | 22 | 51 | 89 |  | Gig-E | 1036 | 2456 | 4364 | These are inbound from servers
[6 empty] | OC-192 | 176 | 408 | 712 | These are inbound from NAS
Total Router Traffic
Per Cost Analysis, OC48's are most cost-effective for non-server interconnects, so these are factored | [6 empty] | Total # Ports Required |  |  |  |  | Total # Cards |  |  | Total # Shelves |  |  | Total # racks |  |  | Power Consumption kWh (total per year) |  |  |  | Year 1 | [6 empty] | Year 2 | [6 empty] | Year 3 | [6 empty] | Total Cost Summary
Router-to-Router (for redundancy and further failover) | [6 empty] | Year 1 | Year 2 | Year 3 |  |  | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  |  | Year 1 | Year 2 | Year 3 | 3-year Total
Assume 1:1 redundancy between shelves (set up as a ring), so a total of four card slots reserved for inter-shelf redundancy; means 4 cards per shelf total. Use OC-192s to maximize the number of in-shelf card failures it can handle. | [5 empty] | Gig-E | 1036 | 2456 | 4364 |  | Gig-E | 130 | 307 | 546 | 10 | 26 | 46 |  |  |  | 61496 | 145224 | 258280 |  | 2494000 | 220000 | 110000 | 22370 | 0 | 2846370 |  | 2128000 | 40000 | 20000 | 39985 | 542800 | 2770785 |  | 3547000 | 200000 | 100000 | 70597 | 976400 | 4893997 |  | Cost | 2846370 | 2770785 | 4893997 | 10511152
[6 empty] | OC-48 | 416 | 982 | 1746 |  | OC-48 | 52 | 123 | 219 | 5 | 11 | 19 |  |  |  | 61496 | 145460 | 258990 | [22 empty] | New Cards | 314 | 322 | 491 | 1127
[6 empty] | OC-192 | 176 | 408 | 712 |  | OC-192 (NAS) | 44 | 102 | 178 | 22 | 26 | 45 |  |  |  | 104069 | 241251 | 421006 | [22 empty] | New Shelves | 22 | 4 | 20 | 46
[6 empty] | Totals | 1452 | 3438 | 6110 |  | OC-192 (R2R) | 88 | 104 | 184 | NA | NA | NA |  |  |  | 208138 | 245981 | 435197 | [22 empty] | New Racks | 22 | 4 | 20 | 46
[11 empty] | Totals | 314 | 636 | 1127 | 22 | 26 | 46 | 22 | 26 | 46 | 435199 | 777916 | 1373473 | [22 empty] | Power | 435199 | 777916 | 1373473 | 2586588
Data Center Costs
This includes costs not directly tied to server/switch equipment.
Assume a Tier III Data Center for availability/reliability
Most of this approach came from Uptime Institute True TCO Calculator
|  | Year 1 | Year 2 | Year 3
Capital Costs
Facility Construction Costs
| Square Footage | 4544 | 9024 | 16704
| Land Costs (assume 5 acres @ $100K/acre) | 500000 | 0 | 0
| kW-Related Infrastructure Costs | 12855615.6543 | 0 | 0
| Other Facility Costs | 595264 | 0 | 0
| Interest | 279017.5931 | 0 | 0
| Architecture/Engineering Fees | 672543.9827
Internet Fiber Last Mile Cost
| Number of Single-Mode Fiber Strands | 1746
| Number of Cables (144 strands/cable) | 13
| Total Cable Length (# cables * fiber run * 110%) | 75504
| Cable Cost | 148742.88
| Installation Costs | 250000
| TOTAL Internet Last Mile | 398742.88 | 0 | 0
| Internal Cabling Cost | 147680 | 0 | 0
| Fire Suppression | 27006.4612 | 0 | 0
| Total Capital Costs | 15475870.5713 | 0 | 0
Annual Operating Expenses
Energy and Power Use/Costs
| Total Electricity Use (kW) | 283.3203 | 611.1263 | 1080.2584
| IT Load (kWh/yr) | 1240943 | 2676733 | 4731532
| Cooling and Auxiliaries (kWh/yr) | 1240943 | 2676733 | 4731532
| Total Consumption (kWh/yr) | 2481886 | 5353466 | 9463064
| Annual Energy Cost | 127568.9404 | 275168.1524 | 486401.4896
| Annual Internet Transit Cost | 655157.7253 | 1435687.5649 | 1932066.8133
| Annual HW Vendor Support Costs | 0 | 918800 | 1580867
| Property Taxes | 154758.7057 | 154758.7057 | 154758.7057
| Total Annual Operating Expenses | 937485.3715 | 2784414.423 | 4154094.0086
Labor Costs
| IT site management staff | 390000 | 401700 | 413751
| Facilities site management staff | 520000 | 535600 | 551668
| Maintenance | 416000 | 428480 | 588298.7552
| Security | 702000 | 723060 | 744751.8
| Janitorial and landscaping | 18176 | 18721.28 | 19282.9184
| Total Labor Costs | 2028000 | 2088840 | 2151505.2
Total Data Center Costs |  | 18441355.9428 | 4873254.423 | 6305599.2086
Labor Estimates
|  |  | IT site | Facilities site
|  |  | Mgmt | Mgmt | Maintenance | Security
| Salary per person | k$/year | 100 | 100 | 80 | 60
| People per shift | # | 3 | 4 | 4 | 3
| Shifts per day | # | 1 | 1 | 1 | 3
| benefits percentage | % | 30% | 30% | 30% | 30%
| Total cost per year | k$/year | 390 | 520 | 416 | 702
| Janitorial and Landscaping Costs |  |  | 4 | per square foot
Note on W50: Crash Davis: Set to the Storage Servers per assumption
Note on AQ50: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W60: Crash Davis: Set to the Storage Servers per assumption
Note on AQ60: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W70: Crash Davis: Set to the Storage Servers per assumption
Note on AQ70: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W81: Crash Davis: Set to the Storage Servers per assumption
Note on AQ81: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on H100: Crash Davis: This is total bw needed /usable bw per card port *2 (for redundancy)
Note on H112: Crash Davis: This is # servers * # NICs per server # servers has built-in-redundancy for BW
Note on H118: Crash Davis: This is total bw needed /usable bw per card port *2 (for redundancy)
Note on B137: Crash Davis: This assumes a total square footage based on a per-rack sf estimate For a Tier III, the standard is 1:1 add'l space compared to electrically active space
Note on B139: Crash Davis: Uptime Institute figure of 23801 per kW of IT Load
Note on B141: Crash Davis: Interest on the Construction and Land Costs @ 2% real discount rate (assumed)
Note on B142: Crash Davis: Assumed at 5% of infrastructure and facility costs
Note on B143: Crash Davis: This is a first year cost, since it is expensive to lay additional fiber later
Note on C144: Crash Davis: Based on max number of internet-to-router OC-48 ports (1 strand per port)
Note on B148: Crash Davis: This is just an approximation; too many variables to establish a basis estimate
Note on B150: Crash Davis: Estimated at the equivalent of $65/sf of electrically active space
Note on B151: Crash Davis: Estimated at $50/sf of electrically active area
Note on B157: Crash Davis: Equal to the IT Load (conservation of energy)
Note on B160: Crash Davis: This is calculated by taking the BW at year-end-BW at start and dividing by 2 as an approximate average bandwidth over the year, then multiplying by the IP transit cost (Mbps/month)
Note on B161: Crash Davis: A % of the cost of prior year total capacity (servers and routers)
Note on B162: Crash Davis: Estimated at 1% of Capital Costs/year
Note on A164: Crash Davis: 3% per annum COLA; Maintenance grows to 4 in year 3 due to increased capacity

## Scenario 3
Scenario 3: General Servers - Encryption and Rate Adaptation
General Notes on Architecture
Server Type (Large, X-Large) selected per service; all servers for a given service are homogenous
With rate adaptation, streaming bit rate songs don't need to be stored. The downloadable file can be stored and rate adapted for all streaming requests.
Assume Rate adaptation is possible on and encrypted file (since, per the project logical architecture, encryption is first
Assume a user always streams the same bit-rate songs (i.e., the user distribution matches the bit-rate distribution of 20/60/20)
Scale on an annual basis not on intermediate 6 month numbers (provides in-rack scalability and redundancy); additional capacity arrives just-in-time
Total Infrastructure Capacity Summary
Infrastructure | Total Capacity (Cum) | Year 1 | Year 2 | Year 3
| Servers | 657 | 1083 | 1754
| Router Cards | 441 | 765 | 1256
| Router Shelves | 15 | 25 | 40
| Racks | 110 | 182 | 294
Total Cost Summary
Equipment Costs (Annual) |  | Year 1 | Year 2 | Year 3
| Servers | 1543950 | 1021122 | 1640554.74
| Routers | 2775000 | 2000000 | 3025000
| Racks | 550000 | 360000 | 560000
| Total Equipment Costs | 4868950 | 3381122 | 5225554.74
Operating Costs
| Power | 190737.3816 | 319194.8224 | 518851.0292
| Labor | 2028000 | 2088840 | 2151505.2
| Other Expenses | 823421.0708 | 2467740.9103 | 3568344.5588
| Capital Costs (Land and Facility Construction) | 16826334.5449 | 0 | 0
| Total Operating Costs | 19868492.9973 | 4875775.7327 | 6238700.788
Total Lifecycle Cost | 44458596.258 | 24737442.9973 | 8256897.7327 | 11464255.528
Servers
Streaming and Download Servers
[6 empty] | Resource Calculations | [31 empty] | Cost Calculations
Servers do not perform the high bit-rate song before sending to rate adaptation; both rate adaptation and encryption occur (in that order) on those servers; bandwidth based on sending high-rate songs | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
Streaming | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 489929 | 90409 | 304377.16 | 884715.16
| Storage (GB) | 230400 | 230400 | 230400 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 154 | 0 | 64 | 218
| TPS | 8384.3812 | 19868.5 | 35323.175 |  | Large | 23 | 15 | 12 | 362 | 104 | 362 | 33 | 824491 |  | Large | 53 | 36 | 27 | 362 | 245 | 362 | 0 | 0 | 824491 |  | Large | 95 | 63 | 48 | 362 | 435 | 435 | 73 | 7 | 990756 |  | Large | 307700 | 165000 | 42379 | 0 | 515079 |  | Large | 0 | 0 | 42379 | 61540 | 103919 | Large | 64556.82 | 35000 | 50925 | 61540 | 212021.82 | 435 | 40 | 2639738 | 831019.82 |  | New Racks | 22 | 0 | 10 | 32
| Bandwidth (Gbps) | 77.2705 | 183.1081 | 325.5384 |  | Xlarge | 10 | 4 | 5 | 154 | 52 | 154 | 22 | 350750 |  | Xlarge | 13 | 15 | 12 | 154 | 123 | 154 | 0 | 0 | 350750 |  | Xlarge | 40 | 27 | 20 | 154 | 218 | 218 | 64 | 10 | 496517 |  | Xlarge | 361900 | 110000 | 18029 | 0 | 489929 |  | Xlarge | 0 | 0 | 18029 | 72380 | 90409 | Xlarge | 156476.16 | 50000 | 25521 | 72380 | 304377.16 | 218 | 32 | 1198017 | 884715.16 | Use XL servers | Power | 350750 | 350750 | 496517 | 1198017
Download Storage Servers
Memory in this scenario (used for encryption) was not evaluated since needed memory volumes are easily satisfied with the number of storage and/or bandwidth-based server quantities | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
Download | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 613677 | 112717 | 227387.9 | 953781.9
| Storage (GB) | 288000 | 288000 | 288000 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 192 | 0 | 35 | 227
| TPS | 1397.3969 | 3311.4167 | 5887.1958 |  | Large | 4 | 3 | 2 | 452 | 108 | 452 | 42 | 1029475 |  | Large | 5 | 3 | 3 | 452 | 255 | 452 | 0 | 0 | 1029475 |  | Large | 8 | 6 | 4 | 452 | 453 | 453 | 1 | 1 | 1031753 |  | Large | 384200 | 210000 | 52915 | 0 | 647115 |  | Large | 0 | 0 | 52915 | 76840 | 129755 | Large | 884.34 | 5000 | 53032 | 76840 | 135756.34 | 453 | 43 | 3090703 | 912626.34 |  | New Racks | 28 | 0 | 5 | 33
| Bandwidth (Gbps) | 80.4901 | 190.7376 | 339.1025 |  | Xlarge | 2 | 2 | 1 | 192 | 54 | 192 | 28 | 437299 |  | Xlarge | 0 | 2 | 1 | 192 | 128 | 192 | 0 | 0 | 437299 |  | Xlarge | 4 | 3 | 2 | 192 | 227 | 227 | 35 | 5 | 517015 |  | Xlarge | 451200 | 140000 | 22477 | 0 | 613677 |  | Xlarge | 0 | 0 | 22477 | 90240 | 112717 | Xlarge | 85572.9 | 25000 | 26575 | 90240 | 227387.9 | 227 | 33 | 1391613 | 953781.9 | Use XL servers | Power | 437299 | 437299 | 517015 | 1391613
Rate Adaptation / Encryption Servers
Rate Adaptation and Ecryption performed in memory; since high-rates don't require adaptation they are encrypted only. Since the Rate Adapters are serving user requests (only transforming files), user capacity is assumed 2x. High-rate song bandwidth in; normal streaming bandwidth out; memory not an issue (BW drives) | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
Download | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 799234 | 1262194 | 1866187.88 | 3927615.88
| Storage (GB) | 0 | 0 | 0 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 251 | 344 | 462 | 1057
| TPS | 8384.3812 | 19868.5 | 35323.175 |  | Large | 12 | 8 | 6 | 0 | 502 | 502 | 46 | 1143355 |  | Large | 27 | 18 | 14 | 0 | 1189 | 1189 | 687 | 63 | 2708066 |  | Large | 48 | 32 | 24 | 0 | 2113 | 2113 | 924 | 84 | 4812569 |  | Large | 426700 | 230000 | 58768 | 0 | 715468 |  | Large | 595629 | 315000 | 139195 | 85340 | 1135164 | Large | 817130.16 | 420000 | 247366 | 204465.8 | 1688961.96 | 2113 | 193 | 8663990 | 3539593.96 |  | New Racks | 36 | 50 | 66 | 152
| Bandwidth (Gbps) | 376.0496 | 891.1261 | 1584.2868 |  | Xlarge | 5 | 4 | 3 | 0 | 251 | 251 | 36 | 571678 |  | Xlarge | 7 | 8 | 6 | 0 | 595 | 595 | 344 | 50 | 1355172 |  | Xlarge | 20 | 14 | 10 | 0 | 1057 | 1057 | 462 | 66 | 2407423 |  | Xlarge | 589850 | 180000 | 29384 | 0 | 799234 |  | Xlarge | 824568 | 250000 | 69656 | 117970 | 1262194 | Xlarge | 1129562.28 | 330000 | 123742 | 282883.6 | 1866187.88 | 1057 | 152 | 4334273 | 3927615.88 | Use XL servers | Power | 571678 | 1355172 | 2407423 | 4334273
Web/App Servers
[38 empty] | Cost Calculations | [6 empty] | Cost Calculations
These handle all the incoming requests (transactions) and route the outbound responses (downloading files only in this scenario) ; they handle all the permission requests directly (ie., no routing to storage server clusters and in memory) | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
[6 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 193024 | 301378 | 445955.2 | 940357.2
| Storage (GB) | 0 | 0 | 0 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 60 | 82 | 110 | 252
| TPS | 15371.3656 | 36425.5833 | 64759.1542 |  | Large | 21 | 14 | 11 | 0 | 120 | 120 | 11 | 273312 |  | Large | 49 | 33 | 25 | 0 | 283 | 283 | 163 | 15 | 644561 |  | Large | 87 | 58 | 44 | 0 | 503 | 503 | 220 | 20 | 1145633 |  | Large | 102000 | 55000 | 14048 | 0 | 171048 |  | Large | 141321 | 75000 | 33130 | 20400 | 269851 | Large | 194554.8 | 100000 | 58886 | 48664.2 | 402105 | 503 | 46 | 2063506 | 843004 |  | New Racks | 9 | 12 | 16 | 37
| Bandwidth (Gbps) | 89.4334 | 211.9307 | 376.7805 |  | Xlarge | 9 | 6 | 5 | 0 | 60 | 60 | 9 | 136656 |  | Xlarge | 12 | 14 | 11 | 0 | 142 | 142 | 82 | 12 | 323419 |  | Xlarge | 36 | 24 | 18 | 0 | 252 | 252 | 110 | 16 | 573955 |  | Xlarge | 141000 | 45000 | 7024 | 0 | 193024 |  | Xlarge | 196554 | 60000 | 16624 | 28200 | 301378 | Xlarge | 268943.4 | 80000 | 29501 | 67510.8 | 445955.2 | 252 | 37 | 1034030 | 940357.2 | Use XL Servers | Power | 136656 | 323419 | 573955 | 1034030
Totals
Sum of all Servers | [37 empty] | Cost Calculations | [6 empty] | Cost Calculations
[6 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [10 empty] | Total Cost Summary
User Interaction | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 2095864 | 1766698 | 2843908.14 | 6706470.14
| Storage (GB) | 518400 | 518400 | 518400 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 657 | 426 | 671 | 1754
| TPS | 33537.525 | 79474 | 141292.7 |  | Large | [5 empty] | 1436 | 132 | 3270633 |  | Large | [5 empty] | 2286 | 850 | 78 | 5206593 |  | Large | [5 empty] | 3504 | 1218 | 112 | 7980711 |  | Large | 1220600 | 660000 | 168110 | 0 | 2048710 |  | Large | 736950 | 390000 | 267619 | 244120 | 1638689 | Large | 1077126.12 | 560000 | 410209 | 391510 | 2438845.12 | [5 empty] | New Racks | 95 | 62 | 97 | 254
| Bandwidth (Gbps) | 623.2435 | 1476.9024 | 2625.7082 |  | Xlarge | [5 empty] | 657 | 95 | 1496383 |  | Xlarge | [5 empty] | 1083 | 426 | 62 | 2466640 |  | Xlarge | [5 empty] | 1754 | 671 | 97 | 3994910 |  | Xlarge | 1543950 | 475000 | 76914 | 0 | 2095864 |  | Xlarge | 1021122 | 310000 | 126786 | 308790 | 1766698 | Xlarge | 1640554.74 | 485000 | 205339 | 513014.4 | 2843908.14 | [5 empty] | Power | 1496383 | 2466640 | 3994910 | 7957933
Routers
Single Tier Network
Use Gig-E to connect all servers to routers
Use fiber (OC-48 or OC-192) to connect router-to-router and router-to-internet
Assume perfect load-balancing between connectivity
Assume following Shelf Configuration: 22 GigE, 6 OC48 and 4 OC192 cards
Assume at any time only 50% of ports are active (fully 1:1 redundancy)
Router-to-Internet
Resource Needs |  | Year 1 | Year 2 | Year 3 |  | Card Type | # Ports Required
| Bandwidth (Gbps) | 388.2125 | 919.9486 | 1635.5289 |  |  | Year 1 | Year 2 | Year 3
[6 empty] | Gig-E | 1036 | 2454 | 4362
[6 empty] | OC-48 | 416 | 982 | 1746
[6 empty] | OC-192 | 104 | 246 | 438
Router-to-Server
Since the servers only have Gig-E NICs, all connections with servers are via Gig-E router cards
# Ports needed determined by the MAX of ports needed based on BW (*2) vs physical NICs on each server
Other transactional messaging (e.g. IPC messages, etc. between servers) is considered negligible and not estimated
Resource Needs |  | Year 1 | Year 2 | Year 3 |  |  | # Ports Required
| Servers | 657 | 1083 | 1754 |  |  | Year 1 | Year 2 | Year 3
[6 empty] | Gig-E | 2628 | 4332 | 7016 | These are inbound from servers
Total Router Traffic
Per Cost Analysis, OC48's are most cost-effective for non-server interconnects, so these are factored | [6 empty] | Total # Ports Required |  |  |  |  | Total # Cards |  |  | Total # Shelves |  |  | Total # racks |  |  | Power Consumption kWh (total per year) |  |  |  | Year 1 | [6 empty] | Year 2 | [6 empty] | Year 3 | [6 empty] | Total Cost Summary
Router-to-Router (for redundancy and further failover) | [6 empty] | Year 1 | Year 2 | Year 3 |  |  | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  |  | Year 1 | Year 2 | Year 3 | 3-year Total
Assume 1:1 redundancy between shelves (set up as a ring), so a total of four card slots reserved for inter-shelf redundancy; means 4 cards per shelf total. Use OC-192s to maximize the number of in-shelf card failures it can handle. | [5 empty] | Gig-E | 2628 | 4332 | 7016 |  | Gig-E | 329 | 542 | 877 | 15 | 25 | 40 |  |  |  | 155631 | 256388 | 414857 |  | 2625000 | 150000 | 75000 | 18455 | 0 | 2868455 |  | 1900000 | 100000 | 50000 | 32813 | 555000 | 2637813 |  | 2875000 | 150000 | 75000 | 54088 | 955000 | 4109088 |  | Cost | 2868455 | 2637813 | 4109088 | 9615356
[6 empty] | OC-48 | 416 | 982 | 1746 |  | OC-48 | 52 | 123 | 219 | 9 | 21 | 37 |  |  |  | 61496 | 145460 | 258990 | [22 empty] | New Cards | 441 | 324 | 491 | 1256
[6 empty] | OC-192 | NA | NA | NA |  | OC-192 | 60 | 100 | 160 | NA | NA | NA |  |  |  | 141912 | 236520 | 378432 | [22 empty] | New Shelves | 15 | 10 | 15 | 40
[6 empty] | Totals | 3044 | 5314 | 8762 |  | Totals | 441 | 765 | 1256 | 15 | 25 | 40 | 15 | 25 | 40 | 359039 | 638368 | 1052279 | [22 empty] | New Racks | 15 | 10 | 15 | 40
[46 empty] | Power | 359039 | 638368 | 1052279 | 2049686
Data Center Costs
This includes costs not directly tied to server/switch equipment.
Assume a Tier III Data Center for availability/reliability
Most of this approach came from Uptime Institute True TCO Calculator
|  | Year 1 | Year 2 | Year 3
Capital Costs
Facility Construction Costs
| Square Footage | 7040 | 11648 | 18816
| Land Costs (assume 5 acres @ $100K/acre) | 500000 | 0 | 0
| kW-Related Infrastructure Costs | 13713258.6061 | 0 | 0
| Other Facility Costs | 922240 | 0 | 0
| Interest | 302709.9721 | 0 | 0
| Architecture/Engineering Fees | 731774.9303
Internet Fiber Last Mile Cost
| Number of Single-Mode Fiber Strands | 1746
| Number of Cables (144 strands/cable) | 13
| Total Cable Length (# cables * fiber run * 110%) | 75504
| Cable Cost | 148742.88
| Installation Costs | 250000
| TOTAL Internet Last Mile | 398742.88 | 0 | 0
| Internal Cabling Cost | 228800 | 0 | 0
| Fire Suppression | 28808.1564 | 0 | 0
| Total Capital Costs | 16826334.5449 | 0 | 0
Annual Operating Expenses
Energy and Power Use/Costs
| Total Electricity Use (kW) | 423.6123 | 708.9059 | 1152.3263
| IT Load (kWh/yr) | 1855422 | 3105008 | 5047189
| Cooling and Auxiliaries (kWh/yr) | 1855422 | 3105008 | 5047189
| Total Consumption (kWh/yr) | 3710844 | 6210016 | 10094378
| Annual Energy Cost | 190737.3816 | 319194.8224 | 518851.0292
| Annual Internet Transit Cost | 655157.7253 | 1435687.5649 | 1932066.8133
| Annual HW Vendor Support Costs | 0 | 863790 | 1468014.4
| Property Taxes | 168263.3454 | 168263.3454 | 168263.3454
| Total Annual Operating Expenses | 1014158.4524 | 2786935.7327 | 4087195.588
Labor Costs
| IT site management staff | 390000 | 401700 | 413751
| Facilities site management staff | 520000 | 535600 | 551668
| Maintenance | 416000 | 428480 | 588298.7552
| Security | 702000 | 723060 | 744751.8
| Janitorial and landscaping | 28160 | 29004.8 | 29874.944
| Total Labor Costs | 2028000 | 2088840 | 2151505.2
Total Data Center Costs |  | 19868492.9973 | 4875775.7327 | 6238700.788
Labor Estimates
|  |  | IT site | Facilities site
|  |  | Mgmt | Mgmt | Maintenance | Security
| Salary per person | k$/year | 100 | 100 | 80 | 60
| People per shift | # | 3 | 4 | 4 | 3
| Shifts per day | # | 1 | 1 | 1 | 3
| benefits percentage | % | 30% | 30% | 30% | 30%
| Total cost per year | k$/year | 390 | 520 | 416 | 702
| Janitorial and Landscaping Costs |  |  | 4 | per square foot
Note on W41: Crash Davis: Set to the Storage Servers per assumption
Note on AQ41: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W51: Crash Davis: Set to the Storage Servers per assumption
Note on AQ51: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W61: Crash Davis: Set to the Storage Servers per assumption
Note on AQ61: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W71: Crash Davis: Set to the Storage Servers per assumption
Note on AQ71: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W82: Crash Davis: Set to the Storage Servers per assumption
Note on AQ82: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on H100: Crash Davis: This is total bw needed /usable bw per card port *2 (for redundancy)
Note on H112: Crash Davis: This is # servers * # NICs per server # servers has built-in-redundancy for BW
Note on H118: Crash Davis: This is total bw needed /usable bw per card port *2 (for redundancy)
Note on B136: Crash Davis: This assumes a total square footage based on a per-rack sf estimate For a Tier III, the standard is 1:1 add'l space compared to electrically active space
Note on B138: Crash Davis: Uptime Institute figure of 23801 per kW of IT Load
Note on B140: Crash Davis: Interest on the Construction and Land Costs @ 2% real discount rate (assumed)
Note on B141: Crash Davis: Assumed at 5% of infrastructure and facility costs
Note on B142: Crash Davis: This is a first year cost, since it is expensive to lay additional fiber later
Note on C143: Crash Davis: Based on max number of internet-to-router OC-48 ports (1 strand per port)
Note on B147: Crash Davis: This is just an approximation; too many variables to establish a basis estimate
Note on B149: Crash Davis: Estimated at the equivalent of $65/sf of electrically active space
Note on B150: Crash Davis: Estimated at $50/sf of electrically active area
Note on B156: Crash Davis: Equal to the IT Load (conservation of energy)
Note on B159: Crash Davis: This is calculated by taking the BW at year-end-BW at start and dividing by 2 as an approximate average bandwidth over the year, then multiplying by the IP transit cost (Mbps/month)
Note on B160: Crash Davis: A % of the cost of prior year total capacity (servers and routers)
Note on B161: Crash Davis: Estimated at 1% of Capital Costs/year
Note on A163: Crash Davis: 3% per annum COLA; Maintenance grows to 4 in year 3 due to increased capacity

## Scenario 4
Scenario 4: Dedicated Storage Servers - Encryption and Rate Adaptation
General Notes on Architecture
Server Type (Large, X-Large) selected per capability/feature; all servers for a given capability/feature are homogenous
With rate adaptation, the high-bit rate songs must be stored only; others are adapted and stored in memory
Encryption and rate adaptation occurs on same server (at normal user capacity, since not processing transactions)
Scale on an annual basis not on intermediate 6 month numbers (provides in-rack scalability and redundancy); additional capacity arrives just-in-time
Some songs may be cached in memory based on Pareto Principle
Assume active rate is consistent over entire day 24x7x365
Total Infrastructure Capacity Summary
Infrastructure | Total Capacity (Cum) | Year 1 | Year 2 | Year 3
| Servers | 321 | 759 | 1357
| Router Cards | 268 | 620 | 1098
| Router Shelves | 10 | 21 | 37
| Racks | 61 | 140 | 252
Total Cost Summary
Equipment Costs (Annual) |  | Year 1 | Year 2 | Year 3
| Servers | 1543950 | 1021122 | 1640554.74
| Routers | 1860000 | 2346000 | 3222000
| Racks | 525000 | 365000 | 565000
| Total Equipment Costs | 3928950 | 3732122 | 5427554.74
Operating Costs
| Power | 111399.1172 | 258767.646 | 457752.1576
| Labor | 2028000 | 2088840 | 2151505.2
| Other Expenses | 800693.3611 | 2262013.2006 | 3431816.849
| Capital Costs (Land and Facility Construction) | 14553563.5706 | 0 | 0
| Total Operating Costs | 17493656.0489 | 4609620.8466 | 6041074.2066
Total Lifecycle Cost | 41232977.8421 | 21422606.0489 | 8341742.8466 | 11468628.9466
Servers
Streaming and Download Servers
[6 empty] | Resource Calculations | [31 empty] | Cost Calculations
NAS cannot perform the encryption; so, it is moved to the rate adaptation servers; bandwidth based on sending high-rate songs | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
Streaming | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 917521 | 1280547 | 2780582 | 4978650
| Storage (GB) | 230400 | 230400 | 230400 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 5 | 6 | 13 | 24
| TPS | 8384.3812 | 19868.5 | 35323.175 |  | Large | 23 | 15 | 12 | 362 | 104 | 362 | 33 | 824491 |  | Large | 53 | 36 | 27 | 362 | 245 | 362 | 0 | 0 | 824491 |  | Large | 95 | 63 | 48 | 362 | 435 | 435 | 73 | 7 | 990756 |  | Large | 307700 | 165000 | 42379 | 0 | 515079 |  | Large | 0 | 0 | 42379 | 61540 | 103919 | Large | 64556.82 | 35000 | 50925 | 61540 | 212021.82 | 435 | 40 | 2639738 | 831019.82 |  | New Racks | 3 | 3 | 7 | 13
| Bandwidth (Gbps) | 77.2705 | 183.1081 | 325.5384 |  | Xlarge | 10 | 4 | 5 | 154 | 52 | 154 | 22 | 350750 |  | Xlarge | 13 | 15 | 12 | 154 | 123 | 154 | 0 | 0 | 350750 |  | Xlarge | 40 | 27 | 20 | 154 | 218 | 218 | 64 | 10 | 496517 |  | Xlarge | 361900 | 110000 | 18029 | 0 | 489929 |  | Xlarge | 0 | 0 | 18029 | 72380 | 90409 | Xlarge | 156476.16 | 50000 | 25521 | 72380 | 304377.16 | 218 | 32 | 1198017 | 884715.16 |  | Power | 49056 | 107923 | 186413 | 343392
[6 empty] | NAS |  |  |  | 3 | 5 | 5 | 3 | 49056 |  | NAS |  |  |  | 3 | 11 | 11 | 6 | 3 | 107923 |  | NAS |  |  |  | 3 | 19 | 19 | 13 | 7 | 186413 |  | NAS | 900000 | 15000 | 2521 | 0 | 917521 |  | NAS | 1080000 | 15000 | 5547 | 180000 | 1280547 | NAS | 2340000 | 35000 | 9582 | 396000 | 2780582 | 19 | 13 | 343392 | 4978650 | Use NAS
Download Storage Servers
Memory in this scenario (used for encryption) was not evaluated since needed memory volumes are easily satisfied with the number of storage and/or bandwidth-based server quantities | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
Download | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 917521 | 1280547 | 2780582 | 4978650
| Storage (GB) | 288000 | 288000 | 288000 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 5 | 6 | 13 | 24
| TPS | 1397.3969 | 3311.4167 | 5887.1958 |  | Large | 4 | 3 | 2 | 452 | 108 | 452 | 42 | 1029475 |  | Large | 5 | 3 | 3 | 452 | 255 | 452 | 0 | 0 | 1029475 |  | Large | 8 | 6 | 4 | 452 | 453 | 453 | 1 | 1 | 1031753 |  | Large | 384200 | 210000 | 52915 | 0 | 647115 |  | Large | 0 | 0 | 52915 | 76840 | 129755 | Large | 884.34 | 5000 | 53032 | 76840 | 135756.34 | 453 | 43 | 3090703 | 912626.34 |  | New Racks | 3 | 3 | 7 | 13
| Bandwidth (Gbps) | 80.4901 | 190.7376 | 339.1025 |  | Xlarge | 2 | 2 | 1 | 192 | 54 | 192 | 28 | 437299 |  | Xlarge | 0 | 2 | 1 | 192 | 128 | 192 | 0 | 0 | 437299 |  | Xlarge | 4 | 3 | 2 | 192 | 227 | 227 | 35 | 5 | 517015 |  | Xlarge | 451200 | 140000 | 22477 | 0 | 613677 |  | Xlarge | 0 | 0 | 22477 | 90240 | 112717 | Xlarge | 85572.9 | 25000 | 26575 | 90240 | 227387.9 | 227 | 33 | 1391613 | 953781.9 |  | Power | 49056 | 107923 | 186413 | 343392
[6 empty] | NAS |  |  |  | 4 | 5 | 5 | 3 | 49056 |  | NAS |  |  |  | 4 | 11 | 11 | 6 | 3 | 107923 |  | NAS |  |  |  | 4 | 19 | 19 | 13 | 7 | 186413 |  | NAS | 900000 | 15000 | 2521 | 0 | 917521 |  | NAS | 1080000 | 15000 | 5547 | 180000 | 1280547 | NAS | 2340000 | 35000 | 9582 | 396000 | 2780582 | 19 | 13 | 343392 | 4978650 | Use NAS
Rate Adaptation / Encryption Servers
Rate Adaptation performed in memory; since high-rates don't require adaptation they pass through. So, the CPU penalty on 20% of the transactions doesn't apply. High-rate song bandwidth in; normal streaming bandwidth out; memory not an issue (BW drives) | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
Download | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 799234 | 1262194 | 1866187.88 | 3927615.88
| Storage (GB) | 0 | 0 | 0 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 251 | 344 | 462 | 1057
| TPS | 8384.3812 | 19868.5 | 35323.175 |  | Large | 18 | 12 | 9 | 0 | 502 | 502 | 46 | 1143355 |  | Large | 27 | 18 | 14 | 0 | 1189 | 1189 | 687 | 63 | 2708066 |  | Large | 48 | 32 | 24 | 0 | 2113 | 2113 | 924 | 84 | 4812569 |  | Large | 426700 | 230000 | 58768 | 0 | 715468 |  | Large | 595629 | 315000 | 139195 | 85340 | 1135164 | Large | 817130.16 | 420000 | 247366 | 204465.8 | 1688961.96 | 2113 | 193 | 8663990 | 3539593.96 |  | New Racks | 36 | 50 | 66 | 152
| Bandwidth (Gbps) | 376.0496 | 891.1261 | 1584.2868 |  | Xlarge | 8 | 5 | 4 | 0 | 251 | 251 | 36 | 571678 |  | Xlarge | 4 | 8 | 6 | 0 | 595 | 595 | 344 | 50 | 1355172 |  | Xlarge | 20 | 14 | 10 | 0 | 1057 | 1057 | 462 | 66 | 2407423 |  | Xlarge | 589850 | 180000 | 29384 | 0 | 799234 |  | Xlarge | 824568 | 250000 | 69656 | 117970 | 1262194 | Xlarge | 1129562.28 | 330000 | 123742 | 282883.6 | 1866187.88 | 1057 | 152 | 4334273 | 3927615.88 | Use XL servers | Power | 571678 | 1355172 | 2407423 | 4334273
Web/App Servers
[38 empty] | Cost Calculations | [6 empty] | Cost Calculations
These handle all the incoming requests (transactions) and route the outbound responses (downloading files only in this scenario) ; they handle all the permission requests directly (ie., no routing to storage server clusters and in memory) | [5 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [5 empty] | Total Servers | Total Racks | Total Pwr Consumed | Total Costs |  | Total Cost Summary
[6 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 193024 | 301378 | 445955.2 | 940357.2
| Storage (GB) | 0 | 0 | 0 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 60 | 82 | 110 | 252
| TPS | 15371.3656 | 36425.5833 | 64759.1542 |  | Large | 21 | 14 | 11 | 0 | 120 | 120 | 11 | 273312 |  | Large | 49 | 33 | 25 | 0 | 283 | 283 | 163 | 15 | 644561 |  | Large | 87 | 58 | 44 | 0 | 503 | 503 | 220 | 20 | 1145633 |  | Large | 102000 | 55000 | 14048 | 0 | 171048 |  | Large | 141321 | 75000 | 33130 | 20400 | 269851 | Large | 194554.8 | 100000 | 58886 | 48664.2 | 402105 | 503 | 46 | 2063506 | 843004 |  | New Racks | 9 | 12 | 16 | 37
| Bandwidth (Gbps) | 89.4334 | 211.9307 | 376.7805 |  | Xlarge | 9 | 6 | 5 | 0 | 60 | 60 | 9 | 136656 |  | Xlarge | 12 | 14 | 11 | 0 | 142 | 142 | 82 | 12 | 323419 |  | Xlarge | 36 | 24 | 18 | 0 | 252 | 252 | 110 | 16 | 573955 |  | Xlarge | 141000 | 45000 | 7024 | 0 | 193024 |  | Xlarge | 196554 | 60000 | 16624 | 28200 | 301378 | Xlarge | 268943.4 | 80000 | 29501 | 67510.8 | 445955.2 | 252 | 37 | 1034030 | 940357.2 | Use XL Servers | Power | 136656 | 323419 | 573955 | 1034030
Totals
Sum of all Servers | [37 empty] | Cost Calculations | [6 empty] | Cost Calculations
[6 empty] | Year 1 | [9 empty] | Year 2 | [10 empty] | Year 3 | [10 empty] | Year 1 | [6 empty] | Year 2 | [5 empty] | Year 3 | [10 empty] | Total Cost Summary
User Interaction | [5 empty] | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total # Servers | # racks | Power Consumption (kwh/yr) |  | Server Type | Total Number of Servers Needed (Based on Demand Type) |  |  |  |  | Total # Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Number of Servers (Based on Demand Type) |  |  |  |  | Total Servers Needed | # Add'l Servers | # Add'l Racks | Power Consumption (kwh/yr) |  | Server Type | Server Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | Server Type | Add'l Server Cost | Add'l Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost | [6 empty] | Year 1 | Year 2 | Year 3 | 3-year Total
| Needed Resources | Year 1 | Year 2 | Year 3 |  |  | Workload (TPS) |  |  | Storage | Bandwidth | [5 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [6 empty] | Workload (TPS) |  |  | Storage | Bandwidth | [29 empty] | Cost | 2827300 | 4124666 | 7873307.08 | 14825273.08
| Storage (GB) | 518400 | 518400 | 518400 |  |  | 40% | 60% | 80% | [7 empty] | 40% | 60% | 80% | [8 empty] | 40% | 60% | 80% | [31 empty] | New Servers | 321 | 438 | 598 | 1357
| TPS | 33537.525 | 79474 | 141292.7 |  | Large | [5 empty] | 1436 | 132 | 3270633 |  | Large | [5 empty] | 2286 | 850 | 78 | 5206593 |  | Large | [5 empty] | 3504 | 1218 | 112 | 7980711 |  | Large | 1220600 | 660000 | 168110 | 0 | 2048710 |  | Large | 736950 | 390000 | 267619 | 244120 | 1638689 | Large | 1077126.12 | 560000 | 410209 | 391510 | 2438845.12 | [5 empty] | New Racks | 51 | 68 | 96 | 215
| Bandwidth (Gbps) | 623.2435 | 1476.9024 | 2625.7082 |  | Xlarge | [5 empty] | 657 | 95 | 1496383 |  | Xlarge | [5 empty] | 1083 | 426 | 62 | 2466640 |  | Xlarge | [5 empty] | 1754 | 671 | 97 | 3994910 |  | Xlarge | 1543950 | 475000 | 76914 | 0 | 2095864 |  | Xlarge | 1021122 | 310000 | 126786 | 308790 | 1766698 | Xlarge | 1640554.74 | 485000 | 205339 | 513014.4 | 2843908.14 | [5 empty] | Power | 806446 | 1894437 | 3354204 | 6055087
[6 empty] | NAS | [5 empty] | 10 | 6 | 98112 |  | NAS | [5 empty] | 22 | 12 | 6 | 215846 |  | NAS | [5 empty] | 38 | 26 | 14 | 372826 |  | NAS | 1800000 | 30000 | 5042 | 0 | 1835042 |  | NAS | 2160000 | 30000 | 11094 | 360000 | 2561094 | NAS | 4680000 | 70000 | 19164 | 792000 | 5561164
Routers
Single Tier Network
Use Gig-E to connect all servers to routers
Use fiber (OC-48 or OC-192) to connect router-to-router and router-to-internet
Assume perfect load-balancing between connectivity
Assume following Shelf Configuration: 22 GigE, 6 OC48 and 4 OC192 cards
Assume at any time only 50% of ports are active (fully 1:1 redundancy)
Router-to-Internet
Resource Needs |  | Year 1 | Year 2 | Year 3 |  | Card Type | # Ports Required
| Bandwidth (Gbps) | 388.2125 | 919.9486 | 1635.5289 |  |  | Year 1 | Year 2 | Year 3
[6 empty] | Gig-E | 1036 | 2454 | 4362
[6 empty] | OC-48 | 416 | 982 | 1746
[6 empty] | OC-192 | 104 | 246 | 438
Router-to-Server
Since the servers only have Gig-E NICs, all connections with servers are via Gig-E router cards
# Ports needed determined by the MAX of ports needed based on BW (*2) vs physical NICs on each server
Other transactional messaging (e.g. IPC messages, etc. between servers) is considered negligible and not estimated
Resource Needs |  | Year 1 | Year 2 | Year 3 |  |  | # Ports Required
| Xlarge Servers | 311 | 737 | 1309 |  |  | Year 1 | Year 2 | Year 3
| NAS Servers | 10 | 22 | 38 |  | Gig-E | 1244 | 2948 | 5236 | These are inbound from servers
[6 empty] | OC-192 | 80 | 176 | 304
Total Router Traffic
Per Cost Analysis, OC48's are most cost-effective for non-server interconnects, so these are factored | [6 empty] | Total # Ports Required |  |  |  |  | Total # Cards |  |  | Total # Shelves |  |  | Total # racks |  |  | Power Consumption kWh (total per year) |  |  |  | Year 1 | [6 empty] | Year 2 | [6 empty] | Year 3 | [6 empty] | Total Cost Summary
Router-to-Router (for redundancy and further failover) | [6 empty] | Year 1 | Year 2 | Year 3 |  |  | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 | Year 1 | Year 2 | Year 3 |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  | Card Cost | Shelf Cost | Rack Cost | IT Power Cost (yr) | HW Support Costs | Total Year Cost |  |  | Year 1 | Year 2 | Year 3 | 3-year Total
Assume 1:1 redundancy between shelves (set up as a ring), so a total of four card slots reserved for inter-shelf redundancy; means 4 cards per shelf total. Use OC-192s to maximize the number of in-shelf card failures it can handle. | [5 empty] | Gig-E | 1244 | 2948 | 5236 |  | Gig-E | 156 | 369 | 655 | 8 | 17 | 30 |  |  |  | 73795 | 174552 | 309842 |  | 1760000 | 100000 | 50000 | 14249 | 0 | 1924249 |  | 2236000 | 110000 | 55000 | 32010 | 372000 | 2805010 |  | 3062000 | 160000 | 80000 | 56470 | 841200 | 4199670 |  | Cost | 1924249 | 2805010 | 4199670 | 8928929
[6 empty] | OC-48 | 416 | 982 | 1746 |  | OC-48 | 52 | 123 | 219 | 9 | 21 | 37 |  |  |  | 61496 | 145460 | 258990 | [22 empty] | New Cards | 268 | 352 | 478 | 1098
[6 empty] | OC-192 | 80 | 176 | 304 |  | OC-192 (NAS) | 20 | 44 | 76 | 10 | 11 | 19 |  |  |  | 47304 | 104069 | 179756 | [22 empty] | New Shelves | 10 | 11 | 16 | 37
[6 empty] | Totals | 1660 | 3930 | 6982 |  | OC-192 (R2R) | 40 | 84 | 148 | NA | NA | NA |  |  |  | 94608 | 198677 | 350050 | [22 empty] | New Racks | 10 | 11 | 16 | 37
[11 empty] | Totals | 268 | 620 | 1098 | 10 | 21 | 37 | 10 | 21 | 37 | 277203 | 622758 | 1098638 | [22 empty] | Power | 277203 | 622758 | 1098638 | 1998599
Data Center Costs
This includes costs not directly tied to server/switch equipment.
Assume a Tier III Data Center for availability/reliability
Most of this approach came from Uptime Institute True TCO Calculator
|  | Year 1 | Year 2 | Year 3
Capital Costs
Facility Construction Costs
| Square Footage | 3904 | 8960 | 16128
| Land Costs (assume 5 acres @ $100K/acre) | 500000 | 0 | 0
| kW-Related Infrastructure Costs | 12098412.3792 | 0 | 0
| Other Facility Costs | 511424 | 0 | 0
| Interest | 262196.7276 | 0 | 0
| Architecture/Engineering Fees | 630491.819
Internet Fiber Last Mile Cost
| Number of Single-Mode Fiber Strands | 1746
| Number of Cables (144 strands/cable) | 13
| Total Cable Length (# cables * fiber run * 110%) | 75504
| Cable Cost | 148742.88
| Installation Costs | 250000
| TOTAL Internet Last Mile | 398742.88 | 0 | 0
| Internal Cabling Cost | 126880 | 0 | 0
| Fire Suppression | 25415.7648 | 0 | 0
| Total Capital Costs | 14553563.5706 | 0 | 0
Annual Operating Expenses
Energy and Power Use/Costs
| Total Electricity Use (kW) | 247.4084 | 574.7021 | 1016.6306
| IT Load (kWh/yr) | 1083649 | 2517195 | 4452842
| Cooling and Auxiliaries (kWh/yr) | 1083649 | 2517195 | 4452842
| Total Consumption (kWh/yr) | 2167298 | 5034390 | 8905684
| Annual Energy Cost | 111399.1172 | 258767.646 | 457752.1576
| Annual Internet Transit Cost | 655157.7253 | 1435687.5649 | 1932066.8133
| Annual HW Vendor Support Costs | 0 | 680790 | 1354214.4
| Property Taxes | 145535.6357 | 145535.6357 | 145535.6357
| Total Annual Operating Expenses | 912092.4783 | 2520780.8466 | 3889569.0066
Labor Costs
| IT site management staff | 390000 | 401700 | 413751
| Facilities site management staff | 520000 | 535600 | 551668
| Maintenance | 416000 | 428480 | 588298.7552
| Security | 702000 | 723060 | 744751.8
| Janitorial and landscaping | 15616 | 16084.48 | 16567.0144
| Total Labor Costs | 2028000 | 2088840 | 2151505.2
Total Data Center Costs |  | 17493656.0489 | 4609620.8466 | 6041074.2066
Labor Estimates
|  |  | IT site | Facilities site
|  |  | Mgmt | Mgmt | Maintenance | Security
| Salary per person | k$/year | 100 | 100 | 80 | 60
| People per shift | # | 3 | 4 | 4 | 3
| Shifts per day | # | 1 | 1 | 1 | 3
| benefits percentage | % | 30% | 30% | 30% | 30%
| Total cost per year | k$/year | 390 | 520 | 416 | 702
| Janitorial and Landscaping Costs |  |  | 4 | per square foot
Note on W49: Crash Davis: Set to the Storage Servers per assumption
Note on AQ49: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W59: Crash Davis: Set to the Storage Servers per assumption
Note on AQ59: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W69: Crash Davis: Set to the Storage Servers per assumption
Note on AQ69: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W79: Crash Davis: Set to the Storage Servers per assumption
Note on AQ79: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on W90: Crash Davis: Set to the Storage Servers per assumption
Note on AQ90: Crash Davis: There is not HW support costs in year 1 as most HW includes 1 yr support
Note on H109: Crash Davis: This is total bw needed /usable bw per card port *2 (for redundancy)
Note on H121: Crash Davis: This is # servers * # NICs per server # servers has built-in-redundancy for BW
Note on H127: Crash Davis: This is total bw needed /usable bw per card port *2 (for redundancy)
Note on B145: Crash Davis: This assumes a total square footage based on a per-rack sf estimate For a Tier III, the standard is 1:1 add'l space compared to electrically active space
Note on B147: Crash Davis: Uptime Institute figure of 23801 per kW of IT Load
Note on B149: Crash Davis: Interest on the Construction and Land Costs @ 2% real discount rate (assumed)
Note on B150: Crash Davis: Assumed at 5% of infrastructure and facility costs
Note on B151: Crash Davis: This is a first year cost, since it is expensive to lay additional fiber later
Note on C152: Crash Davis: Based on max number of internet-to-router OC-48 ports (1 strand per port)
Note on B156: Crash Davis: This is just an approximation; too many variables to establish a basis estimate
Note on B158: Crash Davis: Estimated at the equivalent of $65/sf of electrically active space
Note on B159: Crash Davis: Estimated at $50/sf of electrically active area
Note on B165: Crash Davis: Equal to the IT Load (conservation of energy)
Note on B168: Crash Davis: This is calculated by taking the BW at year-end-BW at start and dividing by 2 as an approximate average bandwidth over the year, then multiplying by the IP transit cost (Mbps/month)
Note on B169: Crash Davis: A % of the cost of prior year total capacity (servers and routers)
Note on B170: Crash Davis: Estimated at 1% of Capital Costs/year
Note on A172: Crash Davis: 3% per annum COLA; Maintenance grows to 4 in year 3 due to increased capacity

## Server Cost Analysis
General Server Cost Analysis
|  | Cost/Server | Annual Power Consumption (kWh) (@80%) | Cost per Transaction per Second (CPU) (@80% utilization) | [11 empty] | Lifetime Costs
|  |  |  | 2000 | TPS |  |  |  | Initial (Non-Recurring) Costs |  |  |  | Annual (Recurring) Costs
|  |  |  | # TPS | # servers needed | # racks needed | Router Cards needed | Total kWh/yr | Total Server Cost | Total Rack Cost | Total Router Card Cost | Total Purchase Costs | Annual Power Cost | Annual HW Support Costs | Total Annual Costs | Year 1 | Year 2 | Year 3 | Total
| Large | 850 | 4555.2 | 1500 | 2 | 0.14286 | NA | 9110.4 | 1700 | 714.2857 | 0 | 2414.2857 | 468.2746 | 340 | 808.2746 | 2882.5603 | 808.2746 | 808.2746 | 4499.1094 | 2000 TPS is break-even between servers; any TPS needs greater than 2000 favor the Xlarge servers
| Xlarge | 2350 | 5088 | 3600 | 1 | 0.14286 | NA | 5088 | 2350 | 714.2857 | 0 | 3064.2857 | 261.5232 | 470 | 731.5232 | 3325.8089 | 731.5232 | 731.5232 | 4788.8553
|  | Cost/Server | Annual Power Consumption (kWh) (@80%) | Cost for Storage (@80% utilization) | [11 empty] | Lifetime Costs
|  |  |  | 2000 | GB |  |  |  | Initial (Non-Recurring) Costs |  |  |  | Annual (Recurring) Costs
|  |  |  | Usable Storage (GB) | # servers needed | # racks needed | Router Cards needed | Total kWh/yr | Total Server Cost | Total Rack Cost | Total Router Card Cost | Total Purchase Costs | Annual Power Cost | Annual HW Support Costs | Total Annual Costs | Year 1 | Year 2 | Year 3 | Total
| Large | 850 | 4555.2 | 637.5 | 4 | 0.28571 | NA | 18220.8 | 3400 | 1428.5714 | 0 | 4828.5714 | 936.5491 | 680 | 1616.5491 | 5765.1205 | 1616.5491 | 1616.5491 | 8998.2188 | 2000 GB is break-even between servers; any storage needs greater than 2000 favor Xlarge servers
| Xlarge | 2350 | 5088 | 1500 | 2 | 0.28571 | NA | 10176 | 4700 | 1428.5714 | 0 | 6128.5714 | 523.0464 | 940 | 1463.0464 | 6651.6178 | 1463.0464 | 1463.0464 | 9577.7106
|  | Cost/Server | Annual Power Consumption (kWh) (@80%) | Cost Bandwidth (Gbps) | [11 empty] | Lifetime Costs
|  |  |  | 1000 | Gbps |  |  |  | Initial (Non-Recurring) Costs |  |  |  | Annual (Recurring) Costs
|  |  |  | Usable BW (Gbps) | # servers needed | # racks needed | Router Cards needed | Total kWh/yr | Total Server Cost | Total Rack Cost | Total Router Card Cost | Total Purchase Costs | Annual Power Cost | Annual HW Support Costs | Total Annual Costs | Year 1 | Year 2 | Year 3 | Total
| Large | 850 | 4555.2 | 0.75 | 1334 | 95.2857 | 333.5 | 6076636.8 | 1133900 | 476428.5714 | 1667500 | 3277828.5714 | 312339.1315 | 560280 | 872619.1315 | 3590167.7029 | 872619.1315 | 872619.1315 | 5335405.966 | Servers are largely interchangeable cost-wise
| Xlarge | 2350 | 5088 | 1.5 | 667 | 95.2857 | 333.5 | 3393696 | 1567450 | 476428.5714 | 1667500 | 3711378.5714 | 174435.9744 | 646990 | 821425.9744 | 3885814.5458 | 821425.9744 | 821425.9744 | 5528666.4946
Router Cost Analysis
|  | Cost/Card | Annual Power Consumption (kWh) (@80%) | Cost per Gbps | [11 empty] | Lifetime Costs
|  |  |  | 500 | Gbps |  |  |  | Initial (Non-Recurring) Costs |  |  |  | Annual (Recurring) Costs
|  |  |  | Usable BW/card | # cards needed | # racks needed |  | Total kWh/yr | Total Card Cost | Total Rack Cost |  | Total Purchase Costs | Annual Power Cost | Annual HW Support Costs | Total Annual Costs | Year 1 | Year 2 | Year 3 | Total
| Gig-E | 5000 | 686.88 | 6 | 84 | 1.5 |  | 57697.92 | 420000 | 7500 |  | 427500 | 2965.6731 | 84000 | 86965.6731 | 430465.6731 | 86965.6731 | 86965.6731 | 604397.0193
| OC-48 | 5000 | 1717.2 | 15 | 34 | 0.60714 |  | 58384.8 | 170000 | 3035.7143 |  | 173035.7143 | 3000.9787 | 34000 | 37000.9787 | 176036.693 | 37000.9787 | 37000.9787 | 250038.6504 | Any bandwidths greater than 7 Gbps favor OC-48; Gig-E should be used for bandwidths below this; OC-192s may be used to limit port use for inter-switch connections for redundancy
| OC-192 | 12000 | 4730.4 | 30 | 17 | 0.30357 |  | 80416.8 | 204000 | 1517.8571 |  | 205517.8571 | 4133.4235 | 40800 | 44933.4235 | 209651.2807 | 44933.4235 | 44933.4235 | 299518.1277
Note on S6: Crash Davis: Does NOT include HW Support (included in purchase cost)
Note on S13: Crash Davis: Does NOT include HW Support (included in purchase cost)
Note on S20: Crash Davis: Does NOT include HW Support (included in purchase cost)
Note on S32: Crash Davis: Does NOT include HW Support (included in purchase cost)

## Constants
Data Constants
# Songs in Library | 40000000
Total Requests/User | Per Hour | Per Second
| 44 | 0.012
Streaming Service Constants | Low Bit Rate (kbps) | Std Bit Rate (kbps) | High Bit Rate (kbps) | % Low Bit Rate | % Std Bit Rate | % High Bit Rate | Song Duration (s) | Requests (/user/hr) | % Total Reqs
| 112 | 192 | 240 | 20% | 60% | 20% | 192 | 24 | 54.55%
Download Service Constants | Song Size (GB) | Requests (/user/hr) | % Total Reqs
| 0.0072 | 4 | 9.091%
Permission Request Service | Request Size (GB) | Requests (/user/hr) | % Total Reqs
Permission Percent of Requests | 0.0002 | 16 | 36.36%
Server Limits | CPU | Disk | Memory | Bandwidth
| 80% | 75% | 80% | 75%
General Purpose Server Specifications
| #RUs | # Cores | Usable RAM (GB) | Usable Disk (GB) | Usable BW (Gbps) | Gig-E Ports | Transactions per Second (Workload) |  |  |  | Max Active Users (Capacity) |  |  |  | Power Consumption (kW) |  |  |  | Servers/Rack |  |  |  | Cost ($)
[7 empty] | 40% CPU | 60% CPU | 80% CPU | 100% CPU | 40% CPU | 60% CPU | 80% CPU | 100% CPU | 40% CPU | 60% CPU | 80% CPU | 100% CPU | 40% CPU | 60% CPU | 80% CPU | 100% CPU
Large | 3 | 4 | 6.4 | 637.5 | 0.75 | 2 | 750 | 1125 | 1500 | 1875 | 62500 | 93750 | 125000 | 156250 | 0.13 | 0.195 | 0.26 | 0.325 | 14 | 14 | 11 | 9 | 850
Xlarge | 6 | 8 | 25.6 | 1500 | 1.5 | 4 | 1800 | 2700 | 3600 | 4500 | 150000 | 225000 | 300000 | 375000 | 0.2 | 0.3 | 0.4 | 0.5 | 7 | 7 | 7 | 6 | 2350
NAS Specifications (Dell EMC Isilon H400) | #RUs | Usable Disk (GB) | 10 GbE Ports | Usable BW (Gbps) | Power (kW) | Cost | Units/Rack
| 4 | 90000 | 8 | 18 | 1.12 | 180000 | 2
Router/Switch Specifications
For Power, assume 9W/Gbps | Shelf Cost | Shelf RUs | Usable Shelf Slots | Line Cards
|  |  |  | Gig-E |  |  |  | OC-48 |  |  |  | OC-192
|  |  |  | Usable Ports/Card | Usable BW (Gbps) / port | Power (kW) | Cost | Ports/Card | Usable BW (Gbps) / port | Power (kW) | Cost | Ports/Card | Usable BW (Gbps) / port | Power (kW) | Cost
| 10000 | 21 | 28 | 8 | 0.75 | 0.054 | 5000 | 8 | 1.875 | 0.135 | 5000 | 4 | 7.5 | 0.27 | 12000
Rack Constants (these are maximums) | #RUs | Power (kW) | Cost (est)
| 42 | 3 | 5000
Data Center Cost Constants
HW/IT Support (% of original cost) | 20% | Assumed to be a percentage of original purchase cost from year 2 on (1st year support included in purchase price)
Square Feet per rack | 32
Power Cost ($/kwh) | 0.0514
Internet Transit Costs ($/Mbps/month) | 0.45
Internet Fiber Run (distance, ft) | 5280
Internet Fiber Cable Cost (per foot) | 1.97
Land Cost / acre (commercial, Dallas-area) | 100000
Acres of Land | 5
Fire Suppression ($/sf) | 50
Property Tax Rate | 1%
Note on F24: Crash Davis: Server BW based on 1:1 redundancy, so total bandwidth is halved then limited to 75% efficiency
Note on T24: Crash Davis: This is the rounded DOWN minimum between power-based and RU-based calculations at each level
Note on D33: Crash Davis: Total slots are 32; however, 4 are reserved for inter-shelf connectivity for redundancy/availability